Copyright 2013 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 078443 - JOINT FIRESTOPPING

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

SUMMARY

Section Includes:

Joints in or between fire-resistance-rated constructions.

Joints at exterior curtain-wall/floor intersections.

Joints in smoke barriers.

PREINSTALLATION MEETINGS

Preinstallation Conference: Conduct conference at [Project site] <Insert location>.

ACTION SUBMITTALS

Product Data: For each type of product.

LEED Submittals:

"Product Data for Credit IEQ 4.1" Subparagraph below applies to LEED-NC, LEED-CI, and LEED-CS; coordinate with requirements selected in Part 2.

Product Data for Credit IEQ 4.1: For joint firestopping system sealants, documentation including printed statement of VOC content.

"Laboratory Test Reports for Credit IEQ 4.1" Subparagraph below applies to LEED for Schools.

Laboratory Test Reports for Credit IEQ 4.1: For joint firestopping system sealants, documentation indicating that products comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Product Schedule: For each joint firestopping system. Include location, illustration of firestopping system, and design designation of qualified testing agency.

Retain "Engineering Judgments" Subparagraph below only after verifying that authorities having jurisdiction will accept modifications handled by method in subparagraph.

Engineering Judgments: Where Project conditions require modification to a qualified testing agency's illustration for a particular joint firestopping system condition, submit illustration, with modifications marked, approved by joint firestopping system manufacturer's fire-protection engineer as an engineering judgment or equivalent fire-resistance-rated assembly.

INFORMATIONAL SUBMITTALS

Product test reports.

CLOSEOUT SUBMITTALS

Installer Certificates: From Installer indicating that joint firestopping systems have been installed in compliance with requirements and manufacturer's written instructions.

QUALITY ASSURANCE

If retaining "Installer Qualifications" Paragraph below, verify that installers are available to perform work in Project location. A list of FM Global-approved firestop contractors may be found in FM Global's "Building Materials Approval Guide," and a list of UL-qualified firestop contractors may be found on www.ul.com/contractor. A list of firestop contractors who are approved or qualified and are FCIA members may be found at www.fcia.org.

Installer Qualifications: A firm that has been approved by FM Global according to FM Global 4991, "Approval of Firestop Contractors," or been evaluated by UL and found to comply with UL's "Qualified Firestop Contractor Program Requirements."

PRODUCTS

Manufacturers and products listed in SpecAgent and Masterworks Paragraph Builder are neither recommended nor endorsed by the AIA or ARCOM. Before inserting names, verify that manufacturers and products listed there comply with requirements retained or revised in descriptions and are both available and suitable for the intended applications. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

PERFORMANCE REQUIREMENTS

Fire-Test-Response Characteristics:

Perform joint firestopping system tests by a qualified testing agency acceptable to authorities having jurisdiction.

Test per testing standards referenced in "Joint Firestopping Systems" Article. Provide rated systems complying with the following requirements:

Joint firestopping systems shall bear classification marking of a qualified testing agency.

Retain only those subparagraphs below that reference the directories of testing agency or agencies approved by authorities having jurisdiction.

UL in its "Fire Resistance Directory."

Intertek Group in its "Directory of Listed Building Products."

<Insert name of qualified testing agency>.

JOINT FIRESTOPPING SYSTEMS

Joint Firestopping Systems: Systems that resist spread of fire, passage of smoke and other gases, and maintain original fire-resistance rating of assemblies in or between which joint firestopping systems are installed. Joint firestopping systems shall accommodate building movements without impairing their ability to resist the passage of fire and hot gases.

Joints in or between Fire-Resistance-Rated Construction: Provide joint firestopping systems with ratings determined per ASTM E 1966 or UL 2079.

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Fire-Resistance Rating: Equal to or exceeding the fire-resistance rating of the wall, floor, or roof in or between which it is installed.

Retain "Joints at Exterior Curtain-Wall/Floor Intersections" Paragraph below if exterior curtain-wall/floor intersections are included in Project and indicate locations on Drawings.

Joints at Exterior Curtain-Wall/Floor Intersections: Provide joint firestopping systems with rating determined per ASTM E 2307.

<Double click here to find, evaluate, and insert list of manufacturers and products.>

F-Rating: Equal to or exceeding the fire-resistance rating of the floor assembly.

Retain "Joints in Smoke Barriers" Paragraph below if smoke barriers are included in Project and indicate locations on Drawings. Coordinate with the Joint Firestopping System Schedule.

Joints in Smoke Barriers: Provide fire-resistive joint systems with ratings determined per UL 2079 based on testing at a positive pressure differential of 0.30-inch wg (74.7 Pa).

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Rating in "L-Rating" Subparagraph below indicates resistance to air leakage.

L-Rating: Not exceeding 5.0 cfm/ft. (0.00775 cu. m/s x m) of joint at both ambient and elevated temperatures.

Exposed Joint Firestopping Systems: Flame-spread and smoke-developed indexes of less than 25 and 450, respectively, as determined per ASTM E 84.

Retain "VOC Content" Paragraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.1. Coordinate with product selection in other Part 2 articles to ensure that products selected comply.

VOC Content: Fire-resistive joint system sealants shall comply with the following limits for VOC content:

Architectural Sealants: 250 g/L.

Sealant Primers for Nonporous Substrates: 250 g/L.

Sealant Primers for Porous Substrates: 775 g/L.

Retain "Low-Emitting Materials" Paragraph below if required for LEED for Schools Credit IEQ 4.1.

Low-Emitting Materials: Fire-resistive joint system sealants shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Accessories: Provide components of fire-resistive joint systems, including primers and forming materials, that are needed to install elastomeric fill materials and to maintain ratings required. Use only components specified by joint firestopping system manufacturer and approved by the qualified testing agency for conditions indicated.

EXECUTION

INSTALLATION

Examine substrates and conditions, with Installer present, for compliance with requirements for joint configurations, substrates, and other conditions affecting performance of the Work.

General: Install fire-resistive joint systems to comply with manufacturer's written installation instructions and published drawings for products and applications indicated.

Install forming materials and other accessories of types required to support elastomeric fill materials during their application and in position needed to produce cross-sectional shapes and depths required to achieve fire ratings indicated.

After installing elastomeric fill materials and allowing them to fully cure, remove combustible forming materials and other accessories not indicated as permanent components of fire-resistive joint system.

Install elastomeric fill materials for fire-resistive joint systems by proven techniques to produce the following results:

Elastomeric fill voids and cavities formed by joints and forming materials as required to achieve fire-resistance ratings indicated.

Apply elastomeric fill materials so they contact and adhere to substrates formed by joints.

For elastomeric fill materials that will remain exposed after completing the Work, finish to produce smooth, uniform surfaces that are flush with adjoining finishes.

IDENTIFICATION

Retain "Joint Identification" Paragraph below if required. See Section 078413 "Penetration Firestopping" for wall identification. Individual joint firestopping system labeling may not be required by authorities having jurisdiction if walls are identified, but labeling is useful if joint firestopping systems must be replaced.

Joint Identification: Identify joint firestopping systems with legible metal or plastic labels. Attach labels permanently to surfaces adjacent to and within 6 inches (150 mm) of joint edge so labels are visible to anyone seeking to remove or joint firestopping system. Use mechanical fasteners or self-adhering-type labels with adhesives capable of permanently bonding labels to surfaces on which labels are placed. Include the following information on labels:

The words "Warning - Joint Firestopping - Do Not Disturb. Notify Building Management of Any Damage."

Contractor's name, address, and phone number.

Designation of applicable testing agency.

Date of installation.

Manufacturer's name.

Installer's name.

FIELD QUALITY CONTROL

If required, inspection of joint firestopping systems in this article is performed according to ASTM E 2393, "On-Site Inspection of Installed Fire-Resistive Joint Systems." To prevent conflicts of interest, ASTM E 2393 precludes making Contractor responsible for engaging the testing agency. Inspectors may verify compliance by destructive examination of some completed installations.

Inspecting Agency: Owner will engage a qualified testing agency to perform tests and inspections according to ASTM E 2393.

Where deficiencies are found or joint firestopping systems are damaged or removed due to testing, repair or replace joint firestopping systems so they comply with requirements.

Proceed with enclosing joint firestopping systems with other construction only after inspection reports are issued and installations comply with requirements.

END OF SECTION 078443