SECTION 23 05 90 – contractor coordination with testing, adjusting, and balancing

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

Specifications throughout all Divisions of the Project Manual are directly applicable to this Section, and this Section is directly applicable to them.

SUMMARY

Perform all Work required to prepare the building HVAC systems for testing, adjusting, and balancing (TAB) Work indicated by the Contract Documents, including the following:

Preparation of air systems for testing, adjusting and balancing.

Preparation of hydronic and steam systems for testing, adjusting and balancing.

Providing materials and labor to assist TAB Firm in meeting testing, adjusting and balancing requirements.

Testing, adjusting and balancing of the air conditioning systems and related ancillary equipment will be performed by a technically qualified TAB Firm.   The preparation for and corrections necessary for the testing, adjusting and balancing of these systems, as described herein, are the responsibility of this Contractor.

Make any changes or replacements to the sheaves, belts, dampers, valves, etc. required for correct balance as advised by the TAB Firm, at no additional cost to the Owner.

REFERENCE STANDARDS

The latest published edition of a reference shall be applicable to this Project unless identified by a specific edition date.

All reference amendments adopted prior to the effective date of this Contract shall be applicable to this Project.

All materials, installation and workmanship shall comply with the applicable requirements and standards addressed within the following references:

AABC:  National Standards for Testing and Balancing Heating, Ventilating and Air Conditioning Systems.

AABC:  Testing and Balancing Procedures.

ASHRAE HVAC Applications Chapter 37:  Testing, Adjusting and Balancing.

ANSI/ASHRAE Standard 111: Practices for Measurement, Testing, Adjusting and Balancing of Buildings, Heating, Ventilation, Air Conditioning and Refrigeration Systems.

quality assurance

Provide and coordinate the services of qualified, responsible Subcontractors, suppliers and personnel as required to correct, repair, and/or replace any and all deficient items or conditions found during the course of this project, including during the testing, adjusting and balancing period.

In order that systems may be properly tested, adjusted, and balanced, the Contractor shall operate systems at Contractor’s expense for the length of time necessary to properly verify the systems’ completion and readiness for TAB.

Project Contract completion schedules shall allow for sufficient time to permit the completion of TAB services prior to Owner occupancy.  Allow adequate time for the testing and balancing activities during the construction period and prior to Substantial Completion.

PRODUCTS

GENERAL

None used.

EXECUTION

preparation

Contractor shall be responsible to prepare the building heating, ventilating, and air conditioning systems ready for TAB when scheduled.

Operational readiness requires that construction status of the building will permit the closing of doors, windows, ceilings installed, etc., to obtain simulated or projected operating conditions.

Notification of System Readiness:

Upon completion of the system installation Work, the Contractor shall notify the Owner and TAB Firm in writing, certifying that the Work has been accomplished and that the air conditioning systems are in operational readiness for testing, adjusting, and balancing.

TAB Firm shall notify the Contractor of TAB Firm’s readiness for balancing.

Should the TAB Firm be notified as described above, and the TAB Work commenced and the systems are found NOT to be in readiness or a dispute occurs as to the readiness of the systems, the Contractor shall request an inspection be made by a duly appointed representative of the Owner, Architect, TAB Firm and the Contractor.  This inspection will establish to the satisfaction of the represented parties whether or not the systems meet the basic requirements for TAB services.  Should the inspection reveal the TAB services notification to have been premature, all cost of the inspection and wasted Work accomplished by the TAB Firm shall be the responsibility of the Contractor.

INSTALLATION

Installation shall meet or exceed all applicable federal, state and local requirements, referenced standards and conform to codes and ordinances of authorities having jurisdiction.

All installation shall be in accordance with manufacturer’s published recommendations.

Allow sufficient time for the TAB Firm to perform TAB Firm’s Work within the Project schedule.  Complete installation Work by system or floor, whichever is the most efficient for scheduling.  Develop the Project schedule in close coordination with the TAB Firm.

The Drawings and Specifications indicate valves, dampers and miscellaneous adjustment devices for the purpose of adjustment to obtain optimum operating conditions.  Install these devices in a manner that will leave the devices accessible and readily able to be adjusted. Immediately correct any malfunction encountered that the TAB Firm reports so that the balancing Work can proceed with minimal delay.

Contractor shall promptly correct deficiencies of materials and workmanship identified as delaying completion of TAB Work.

SYSTEMS VERIFICATION

Air Distribution Systems:

Verify installation for conformity to the Contract Documents.  All supply, return, and exhaust ducts shall be terminated and pressure tested for leakage as required by the Contract Documents.

All volume, smoke and fire/smoke dampers are properly located and functional. Dampers serving requirements of minimum and maximum outside, return, and relief air shall provide tight closure and full opening, smooth and free operation.

All supply, return, exhaust and transfer grilles, registers, diffusers and terminal devices are installed and airflow at each device shall be verified.

Air handling systems, units and associated apparatus, such as heating and cooling coils, filter sections, access doors, etc., shall be sealed or blanked-off to eliminate excessive uncontrolled bypass or leakage of air.

All fans (supply, return and exhaust) operating and verified for freedom from vibration, with proper fan rotation and belt tension. Heater elements in motor starters are of proper size and rating. Record motor amperage and voltage on each phase at Start-up and running, and verify they do not exceed nameplate ratings.

All single and/or double duct variable and constant volume terminal units ("mixing boxes") shall be installed and functional (i.e. controls functioning).

Duct systems and air handling units and coils are clean and free of debris.

Air systems are pressure independent and can be tested by floor, riser, system, etc. but once the all systems are installed, the total flows and system tracking will require final testing, adjusting and balancing.

Water Circulating Systems:

Check and verify pump alignment and rotation.

Open all valves to their full open position, close bypass stop valves.  Set mixing valves to full-flow through systems components.  After the system is flushed and checked for proper operation, remove and clean all strainers.  Repeat the operation until circulating water is clean.

Record the amperage of each pump motor on each phase and voltage after reaching rated speed.  Readings shall not exceed nameplate rating.

Verify that the electrical heater elements are of the proper size and rating.

All water circulating systems shall be full and free of air.  Expansion tanks shall be set for proper water level and all air vents shall be installed at high points of systems and operating freely.  Systems shall be cleaned and flushed.  Chemicals shall be added to closed systems to treat piping and inhibit corrosion.

Check and set operating temperatures and other parameters of the heat exchangers and control devices to the design requirements.

Installation and system verification of condenser water, hot water, and chilled water systems must be 100 percent complete prior to balancing.

Building Automation System (BAS):

Verify that all control components are installed in accordance with the Contract Documents and that all control components are functional, including all electrical interlocks, damper sequences, air and water resets, fire and freeze stats, high and low temperature thermostats, safeties, etc.

Verify that all controlling instruments are calibrated and set for design operating conditions with the exception of room thermostats or sensors, which shall be calibrated at the completion of TAB services with cooperation between the TAB Firm and BAS Provider.

BAS Provider shall thoroughly check all controls, sensors, operators, sequences, etc. before notifying the TAB Firm that the building automation system is operational.  The BAS Provider shall provide technical support, including technicians and necessary computers, to the TAB Firm for a complete check of these systems.

BAS Provider shall assist the Contractor with functional performance testing and point-to-point testing back to the main graphics.

BAS Provider, if requested by Owner, shall set-up controls on sample fan powered terminal units at TAB Firm’s office.

END OF SECTION 23 05 90