SECTION 23 34 13 – inline Fans

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

Specifications throughout all Divisions of the Project Manual are directly applicable to this Section, and this Section is directly applicable to them.

SUMMARY

Perform all Work required to provide and install the following fans indicated by the Contract Documents with supplementary items necessary for proper installation.

Tubular centrifugal fans.

Inline centrifugal fans.

Tube axial.

Propeller.

Mixed flow.

Vane axial.

Motors and drives.

Fan accessories.

REFERENCE STANDARDS

The latest published edition of a reference shall be applicable to this Project unless identified by a specific edition date.

All reference amendments adopted prior to the effective date of this Contract shall be applicable to this Project.

All materials, installation and workmanship shall comply with the applicable requirements and standards addressed within the following references:

AFBMA 9 - Load Ratings and Fatigue Life for Ball Bearings.

AFBMA 11 - Load Ratings and Fatigue Life for Roller Bearings.

AMCA 99 - Standards Handbook.

ACMA 203 - Fan Application Manual - Field Performance Measurements.

AMCA 210 - Laboratory Methods of Testing Fans for Rating Purposes.

AMCA 301 - Method of Calculating Fan Sound Ratings from Laboratory Test Data.

ACMA 803 - Site Performance Test Standard - Power Plant and Industrial Fans.

NEMA MG1 - Motors and Generators.

NFPA 70 - National Electrical Code.

SMACNA - HVAC Duct Construction Standards - Metal and Flexible.

QUALITY ASSURANCE

Performance Ratings: Conform to AMCA 210 and bear the AMCA Certified Rating Seal.

Sound Ratings: AMCA 301, tested to AMCA 300, and bear AMCA Certified Sound Rating Seal.

Fabrication: Conform to AMCA 99.

Performance Base:  50 feet above sea level.

Temperature Limit:  Maximum 300 degrees F.

Static and Dynamic Balance:  Eliminate vibration or noise transmission to occupied areas.

SUBMITTALS

Product Data:

Submittal data for approval for all fans of every description furnished under this Section of these Specifications.

Provide literature that indicates dimensions, weights, capacities, ratings, fan performance, gages and finishes of materials, electrical characteristics and connection requirements.

Fan curves with specified operating point clearly plotted.  The recommended range of operation shall be stable.

Fans shall be capable of operating stably at reduced loads imposed by means of variable speed drives, inlet guide vanes or controlling pitch of fan blades.

Data on sound power levels for both fan inlet and outlet at rated capacity.

Data on special coatings and construction where applicable.

Electrical characteristics and connection requirements.

All data on fan accessories.

Operation and Maintenance Data:

Manufacturer's installation instructions and operating and maintenance data.

Submit under provisions of Division 01.

Include instructions for lubrication, motor and drive replacement, spare parts list, and wiring diagrams.

DELIVERY, STORAGE and HANDLING

Deliver, store, protect and handle products to the Project Site under provisions of Division 01 and Division 20.

Accept products on Site in factory-fabricated protective containers or coverings, with factory-installed shipping skids and lifting lugs.  Inspect for damage.

Store in clean dry place and protect from weather and construction traffic.  Handle carefully to avoid damage to components, enclosures, and finish.

Check and maintain equipment on a monthly basis to ensure equipment is being stored in accordance with manufacturer’s recommended practices.  Additionally, during each check, fans and motors shall be rotated and greased and shafts shall be left approximately 180 degrees from that of previous month.  Maintain storage records that indicate these maintenance requirements have been met.

PRODUCTS

GENERAL

All materials shall meet or exceed all applicable referenced standards, federal, state and local requirements, and conform to codes and ordinances of authorities having jurisdiction.

Fans shall be either belt(with tensioner) or direct drive (preferred) as scheduled on the Drawings. Service access door required.

Select fans such that they do not increase motor size, increase noise level, or increase tip speed by more than 10 percent, or increase inlet air velocity by more than 20 percent, from specified criteria.  Provide fans capable of accommodating static pressure variations of plus or minus 10 percent.

Statically and dynamically balance fans to eliminate vibration or noise transmission to occupied areas.

Coat all parts of fan housing, blades, etc., exposed to corrosive air stream with specified material to handle environmental conditions.

Motors and Drives:  Provide motors and drives as required in this Section and as scheduled on Drawings.

Finishes:  Provide finishes as required in this Section for manufacturer and Site-applied as scheduled on Drawings.

Accessories:  Provide with accessories as require in this Section and as scheduled on Drawings.

manufacturers

Chicago.

Greenheck.

Loren-Cook.

Peerless.

Woods.

TUBULAR INLINE CENTRIFUGAL

Backward inclined or airfoil-type centrifugal fan wheel, mounted in a tubular housing with guide vanes for ducted, un-ducted inlet or discharge, or roof-mounted application.  Direct-drive or belt-drive as scheduled on Drawings.

Wheel: Single width, single inlet, steel or aluminum construction with smooth curved inlet flange, heavy backplate, hollow airfoil-type or backwardly inclined or curved blades welded or riveted to flange and backplate, cast aluminum or cast steel hub riveted to backplate and keyed to shaft with set screws and key.

Housing:  Heavy gage steel, continuously welded for all AMCA 99 designated Classes.  Provide continuously welded vanes to straighten discharge air flow and continuously welded, prepunched integral inlet and discharge flanges. For belt drive fans, isolate drive components from the air stream by a continuously welded belt tunnel and a removable bearing cover. Housing shall be adequately braced, designed to minimize turbulence with spun inlet bell. Housing and bearing supports shall be welded structural steel construction designed to prevent vibration and rigidly support the shaft and bearings.

INLINE CENTRIFUGAL FANS

Backward inclined centrifugal fan wheel, mounted in a rectangular housing for ducted application.  Direct-drive or belt-drive as scheduled on Drawings.

Wheel:  Single width, single inlet, steel or aluminum construction with smooth curved inlet flange, heavy backplate, backwardly inclined or curved blades welded or riveted to flange and backplate; cast aluminum or cast steel hub riveted to backplate and keyed to shaft with set screws and key.

Housing:  Bolted or bolted and welded steel construction with spun, aerodynamic inlet cone for plenum-type fan wheel.  Housing shall be configurable for ducted side or front discharge.  Side panels shall be removable for access to the fan wheel and bearings.

TUBE AXIAL

Propeller-type fan wheel, mounted in a tubular housing with no guide vanes for ducted, un-ducted inlet or discharge, or roof-mounted application.  Direct-drive or belt-drive as scheduled on Drawings.

Wheel:  Propeller-type, cast or extruded aluminum, or fabricated reinforced steel, factory fixed pitch, airfoil design. Cast aluminum or cast steel hub keyed and locked to the shaft utilizing two set screws or a taper lock bushing.

Housing: Heavy gage steel, continuously welded for all AMCA 99 designated Classes.  For belt drive fans, isolate the drive components from the air stream by a continuously welded belt tunnel and a removable bearing cover.  Housing shall be adequately braced, designed to minimize turbulence with spun inlet bell. The housing and bearing supports shall be welded structural steel construction designed to prevent vibration and rigidly support the shaft and bearings.

PROPELLER

Propeller-type fan wheel, mounted in a steel frame for wall-mounted, un-ducted inlet or discharge application.  Direct-drive or belt-drive as scheduled on Drawings.

Wheel: Propeller-type, shaped steel or steel reinforced aluminum blade with heavy hubs, statically and dynamically balanced, keyed and locked to the shaft, directly connected to motor or provided with v-belt drive.

Housing: One-piece square steel frame with die formed venturi orifice, mounting flanges and supports with baked enamel finish. Bearings affixed to mounting plate permitting belt tensioning, neoprene vibration isolation between fan assembly and mounting plate.

MIXED FLOW

Mixed flow-type fan wheel, mounted in a tubular housing with guide vanes for ducted, un-ducted inlet or discharge, or roof-mounted application.  Direct-drive or belt-drive as scheduled on Drawings.

Wheel: Mixed flow-type, steel construction with wheel cone, spherical backplate and single thickness cambered blades. Smooth curved, inlet cone specifically matched to the wheel. Hub shall be steel construction keyed and locked to the shaft.

Housing:  Heavy gage steel, continuously welded for all AMCA 99 designated Classes.  Provide continuously welded vanes to straighten discharge air flow and continuously welded, pre-punched integral inlet and discharge flanges. For belt drive fans, isolate the drive components from the air stream by a continuously welded belt tunnel and a removable bearing cover. Housing shall be adequately braced, designed to minimize turbulence with spun inlet bell. Housing and bearing supports shall be welded structural steel construction designed to prevent vibration and rigidly support the shaft and bearings.

VANE AXIAL

Vane axial-type wheel mounted in a tubular housing with guide vanes for ducted, un-ducted inlet or discharge, or roof-mounted application.  Direct-drive or belt-drive as scheduled on Drawings.

Wheel:  Cast and machined aluminum rotor blades and hub with precision machined conical section blade base and hub socket. Blade shall be manually adjustable or in-flight controllable as scheduled on Drawings. Hub shall be keyed and attached to the shaft with a taper lock bushing. Incorporate ball bearing counterbalanced blade and variable pitch assembly into hub with mechanical link to casing exterior mounted actuator, or pneumatic or electric actuator incorporated within hub.

Housing: Heavy gage steel, continuously welded for all AMCA 99 designated Classes.  Provide continuously welded vanes to straighten discharge air flow and continuously welded, pre-punched integral inlet and discharge flanges. For belt drive fans, isolate the drive components from the air stream by a continuously welded belt tunnel and a removable bearing cover. Housing shall be adequately braced, designed to minimize turbulence with spun inlet bell. Housing and bearing supports shall be welded structural steel construction designed to prevent vibration and rigidly support the shaft and bearings.

MOTORS AND DRIVES

Motors:  As indicated, in total compliance with Section 20 05 13 - Motors.

Bearings:  L-10 life at 200,000 hours self-aligning, grease-lubricated ball or roller bearings.

Shafts:  Hot rolled steel, ground and polished, with key-way, protectively coated with lubricating oil.  Provide 316 stainless steel shafts for fume hood or corrosive applications.

V-Belt Drives:  All v-belt drives shall be designed for a minimum of 50 percent overload. Cast iron or steel sheaves, dynamically balanced, keyed.  Variable and adjustable pitch sheaves for motors 15 horsepower and under, selected so required rpm is obtained with sheaves set at mid-position.  Fixed sheave for 20 horsepower and over.  Where more than one belt is required, matched sets shall be used.  Include an additional set of drives for each fan to be used for final adjustments.  After correct speed has been determined with variable sheave, provide fixed sheaves.

Belt Guards:  All belt drives shall be furnished with belt guards.  Fabricate to SMACNA Low Pressure Duct Construction Standards; of 12 gage 3/4-inch diamond mesh wire screen welded to steel angle frame or equivalent, prime coated.  Secure to fan or fan supports without short circuiting vibration isolation, with provision for adjustment of belt tension, lubrication, and use of tachometer with guard in place.

FACTORY-APPLIED FINISHES

Wheels and Impellers:  Steel components shall be finished with a thermally fused polyester coating. Other finishes as required on Drawings.

Housings:

Interior Fans:  Thermally fused polyester coating for steel.  Prime coating is not required for aluminum housings.

Exterior (Outdoor) Fans:  Prior to assembly with minimum 6 mil saltwater-resistant, thermally-fused polyester coating (color selected by Architect).  Coating is not required for aluminum housings.

Corrosive Environment:  Fume hood fans, prior to assembly with minimum 4 mil, high performance epoxy or Heresite coating by fan manufacturer as appropriate for the chemicals being handled.  Provide spark-proof construction where fan handles flammable materials.

ACCESSORIES

Adjustable Inlet Vanes:  Steel construction with blades supported at both ends with two permanently lubricated bearings, variable mechanism out of air stream terminating in single control lever with control shaft for double width fans and locking quadrant.

Inlet Bell:  Bell mouth inlet fabricated of steel with flange.

Outlet Cones:  Fabricated of steel with flanges, outlet area/inlet area ratio of 1.5/1.0, with center pod as recommended by manufacturer.

Dampers:  Welded steel construction consisting of two semi-circular vanes pivoted on oil retaining bearings in short casing section, finished by hot dip galvanizing.  Provide motor actuation.

Thrust Restraints:  Provide thrust restraints where thrust exceeds fan weight for vane and axial fans.

Inlet/Outlet Screens:  Galvanized steel welded grid. Provide where inlet or outlet are unducted.

Access Doors:  Shaped to conform to housing with quick opening latches and gaskets.

Cover:  Provide weatherproof cover for motor and drive where fans are exposed to the weather.

Extended Wiring:  Provide extended wiring for electrical connection at the exterior of the unit for all direct drive applications.

EXECUTION

INSTALLATION

Installation shall meet or exceed all applicable federal, state and local requirements, referenced standards and conform to codes and ordinances of authorities having jurisdiction.

Install in accordance with manufacturer's instructions. Do not operate fans for any purpose until ductwork is clean, filters in place, bearings lubricated and fan has been test run under observation.

Install fans with resilient mountings and flexible electrical leads.  Refer to Section 20 05 48.

Install flexible connections specified in Section 23 33 00 between fan inlet and discharge ductwork.  Ensure metal bands of connectors are parallel with minimum one-inch flex between ductwork and fan while running.

Install fan restraining snubbers as required.  Refer to Section 20 05 48.  Adjust snubbers to prevent tension in flexible connectors when fan is operating.

Provide safety screen where inlet or outlet is exposed.

Provide backdraft dampers on discharge of exhaust fans where indicated.  Refer to Section 23 33 00.

PAINTING

Provide fans with factory finish in accordance with the manufacturer's standard.  Touch up scratches and marks from handling and placement of equipment with masking enamel to match manufacturer's color.

Where exhaust fans are required to have epoxy or Heresite coating, have units factory finished with required number of coats prior to shipping to the Project Site.

Refer to Division 09 for Site-applied finishes.

END OF SECTION 23 34 13