SECTION 23 34 23 – power ventilators

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

Specifications throughout all Divisions of the Project Manual are directly applicable to this Section, and this Section is directly applicable to them.

SUMMARY

Perform all Work required to provide and install the following fans indicated by the Contract Documents with supplementary items necessary for proper installation.

Centrifugal roof, up-blast, and sidewall exhauster.

Centrifugal roof supply fan.

Make-up air unit.

Centrifugal up-blast grease hood exhaust fan.

Tube axial up-blast smoke control exhaust fan.

Motors and drives.

REFERENCE STANDARDS

The latest published edition of a reference shall be applicable to this Project unless identified by a specific edition date.

All reference amendments adopted prior to the effective date of this Contract shall be applicable to this Project.

All materials, installation and workmanship shall comply with the applicable requirements and standards addressed within the following references:

AFBMA 9 - Load Ratings and Fatigue Life for Ball Bearings.

AFBMA 11 - Load Ratings and Fatigue Life for Roller Bearings.

AMCA 99 - Standards Handbook.

ACMA 203 - Fan Application Manual - Field Performance Measurements.

AMCA 204 - Balance Quality and Vibration Levels For Fans

AMCA 210 - Laboratory Methods of Testing Fans for Aerodynamic Performance Rating.

AMCA 300 - Reverberant Room Method for Sound Testing of Fans.

AMCA 301 - Methods for Calculating Fan Sound Ratings from Laboratory Test Data.

NEMA MG1 - Motors and Generators.

NFPA 70 - National Electrical Code.

SMACNA - HVAC Duct Construction Standards - Metal and Flexible.

UL 705 – Power Ventilators.

QUALITY ASSURANCE

Performance Ratings: Conform to AMCA 210 and bear the AMCA Certified Rating Seal.

Sound Ratings: AMCA 301, tested to AMCA 300, and bear AMCA Certified Sound Rating Seal. The sound power levels must not exceed those indicated on Drawings.

Fabrication: Conform to AMCA 99.

Performance Base:  50 feet above sea level.

Fans shall be capable of operating stably at reduced loads imposed by means of variable speed drives, inlet guide vanes or controlling pitch of fan blades.

SUBMITTALS

Product Data:

Submittal data for approval for all fans of every description furnished under this section of these Specifications.

Provide literature that indicates dimensions, weights, capacities, ratings, fan performance, gages and finishes of materials, special coatings and construction, electrical characteristics and connection requirements.

Fan curves with specified operating point clearly plotted.  The recommended range of operation shall be stable.

Data on sound power levels for both fan inlet and outlet at rated capacity.

All data on fan accessories.

Operation and Maintenance Data:

Manufacturer's installation instructions and operating and maintenance data.

Submit under provisions of Division 01.

Include instructions for lubrication, motor and drive replacement, spare parts list, and wiring diagrams.

DELIVERY, STORAGE and HANDLING

Deliver, store, protect and handle products to the Project Site under provisions of Division 01 and Division 20.

Accept products on Site in factory-fabricated protective containers or coverings, with factory-installed shipping skids and lifting lugs.  Inspect for damage.

Store in clean dry place and protect from weather and construction traffic.  Handle carefully to avoid damage to components, enclosures, and finish.

Check and maintain equipment on a monthly basis to ensure equipment is being stored in accordance with manufacturer’s recommended practices.  Additionally, during each check, fans and motors shall be rotated and greased and shafts shall be left approximately 180 degrees from that of previous month.  Maintain storage records that indicate these maintenance requirements have been met.

PRODUCTS

GENERAL

All materials shall meet or exceed all applicable referenced standards, federal, state and local requirements, and conform to codes and ordinances of authorities having jurisdiction.

Fans shall be either belt or direct drive as scheduled on Drawings.

Select fans such that they do not increase motor size, increase noise level, or increase tip speed by more than 10 percent, or increase inlet air velocity by more than 20 percent, from specified criteria.  Provide fans capable of accommodating static pressure variations of plus or minus 10 percent.

Statically and dynamically balance fans to eliminate vibration or noise transmission to occupied areas.

MANUFACTURERS

Greenheck.

Loren-Cook.

CENTRIFUGAL ROOF, UPBLAST, AND SIDEWALL EXHAUSTER

Backward inclined fan wheel with spun aluminum housing; resilient mounted motor and drive assembly; 16 gage aluminum birdscreen; square base to suit roof curb with continuous curb gaskets; secured to roof curb with cadmium plated or stainless steel bolts and screws.

Roof Curb:  Roof curb shall be coordinated with Owner and Contractor.

Backdraft Damper:  Gravity activated or motorized as indicated.  Where type is not indicated on Drawings or Specifications, provide gravity-activated damper.  Aluminum construction, felt edged with nylon bearings.

Upblast exhausters shall have integral drain trough.

Apply three coats of air-dried Heresite coating by fan manufacturer both internal and external to all roof exhausters for corrosive applications.

CENTRIFUGAL ROOF SUPPLY FAN

Forward curved, double width double inlet, with heavy gage galvanized steel housing; resiliently mounted motor and drive assembly.

Backdraft Damper:  Gravity activated or motorized as indicated.  Where type is not indicated on Drawings or Specifications, provide gravity-activated damper.  Aluminum construction, felt edged with nylon bearings.

Roof Curb:  Roof Curb shall be coordinated with Owner and Contractor.

Filters:  1-inch washable, aluminum, permanent type as furnished with unit.

Hood shall be easily removable for service.

MAKE-UP AIR UNIT

Unit:  Internal frame type construction of G90 galvanized steel with all metal-to-metal surfaces sealed.  All components shall be accessible through removable panels.  Provide unit on prefabricated roof curb.  Installed unit shall be in total compliance with NFPA 96.

Where scheduled, electrical, hot water, steam, gas-fired, chilled water, or direct expansion (DX) coils shall be installed in unit.  Water and steam coils shall be rated in accordance with ARI 410.  Electric coils shall be UL listed with integral heater control cabinet and a separate power connection for the coils.  Downstream components of tempered units shall be double wall construction and insulated in accordance with local energy codes.

Fan Section:  Forward curved, double width double inlet, with heavy gage galvanized steel housing; resiliently mounted motor and drive assembly.

Weather Hood:  Construct of G90 galvanized steel with 1-inch washable, aluminum, permanent type as furnished with unit at unit intake.  Extended weatherhood shall be provided where necessary to ensure minimum ten (10) foot separation between air intake and exhaust air.  Weather hood extensions shall be mounted on adjustable legs.

Electrical:  All electrical components shall be factory wired for a single point power connection.  Control center shall include motor starter, control circuit fusing, control transformer (120VAC), integral door interlocking disconnect switch with separate motor fusing and terminal strip with overload protected motor.

Backdraft Damper:  Gravity activated or motorized as indicated. Where type is not indicated on Drawings or Specifications, provide gravity-activated damper.

CENTRIFUGAL UPBLAST GREESE HOOD EXHAUST FAN

Backward inclined fan wheel, upblast roof fan with spun aluminum housing; resilient mounted motor and drive assembly; square base to suit roof curb with continuous curb gaskets; secured to roof curb with cadmium plated or stainless steel bolts and screws.  External fan wiring.

Roof Curb:  Roof curb shall be coordinated with Owner and Contractor.  Vented roof extension, to maintain fan discharge a minimum of 40-inches above roof, shall be provided by fan manufacturer.

Integral drain trough, cleanout port, and grease trap.

Maximum continuous operating temperature of 400 degrees F.

UL 762 Listed and constructed in compliance with NFPA 96.

TUBE AXIAL UP-BLAST SMOKE CONTROL EXHAUST FAN

Propeller shall be fabricated steel.  Provide with statically and dynamically balanced steel blades and hubs, securely attached to the fan shafts, ground and polish steel fan shafts, galvanized formed channel steel drive frame assembly, deep formed inlet venture fan panels, heavy gage galvanized steel windbands with reinforced edges and bolted seams, square base to suit roof curb gaskets; secured with stainless steel bolts and screws.

Roof curb:  Roof curb shall be coordinated with Owner and Contractor.

Butterfly Dampers:  Steel or aluminum construction based on the required minimum fan speed required to open damper blades.  Provide with magnetic damper latches.

Fan shall meet requirements and be listed for AMCA Certified Rating Seal for sound and air performance and UL Listed Power Ventilators for Smoke Control Systems to include the IRI requirements for 500 degrees F for a minimum of 4 hours, SBCCI Standard Fire Prevention Code for requirements of 1000 degrees F for a minimum of 15 minutes.

AIR CURTAIN UNIT

Rigid welded construction for support at each end without need for intermediate support.  Air curtain fans shall be provided with a weatherproof housing constructed of minimum 16-gage rigid welded steel with baked enamel finish by fan manufacturer.

Fan wheels shall be forward curved, non-overloading, centrifugal type, double inlet, double width with brazed hubs, statically and dynamically balanced.  Wheels and housings shall be galvanized steel.

Each curtain shall be furnished with a door switch to energize curtain whenever the door is open, and actuate the hot water control valve to maintain the temperature set point.   Units shall be provided with factory mounted, factory wired control panels including motor starters, transformer for low voltage door switch and terminal strip for connection to power source. Provide a discharge grille and conduit box for single point connection for fan and controls.

Air curtains shall attain air velocities specified within 2 seconds following activation. Air intake and discharge openings shall be protected by bird screens. Air curtain shall be at least as wide as the opening to be protected.  Air discharge opening shall be so designed and equipped as to permit outward adjustment of the discharge air. Installation and adjustment shall be in accordance with the manufacturer's written instructions.  Interior surfaces of the air curtain shall be accessible for cleaning.

Fan noise levels shall not exceed 45 dBA when measured at a distance of ten (10) feet from fan discharge opening.

Air curtains designed for use in service entranceways shall develop an air curtain not less than three (3) inches thick at the discharge nozzle. The air velocity shall not be less than 1600 fpm across the entire entryway when measured 3 feet above the floor.

Where scheduled, include hot water coils with copper tubes and copper fins. Coil shall be rated at 230 psig and 300 degrees F with capacities per ARI 410.  Provide UL approved, factory-mounted and factory-wired electric coils where scheduled.

Provide control panel with motor starter, terminal strip, motor overloads, and control transformer. Provide field adjustable time delay relay, ON-OFF-AUTOMATIC switch.

MOTORS AND DRIVES (ALL UNITS UNLESS OTHERWISE SPECIFIED)

Motors:  In total compliance with motors and controllers Specification sections.

Disconnect Switches:  Provide for each fan under Division 26.  No switches shall be provided in fan housing.  All disconnects shall be external to fan housing.

Bearings:  L-10 life at 200,000 hours self-aligning, ball or roller bearings.

Shafts:  Hot rolled steel, ground and polished, with key-way, protectively coated with lubricating oil.  Provide 316 stainless steel shafts for corrosive applications.

Belt Drive:  All belt drives shall be designed for a minimum of 50 percent overload. Cast iron or steel sheaves, dynamically balanced, keyed.  Variable and adjustable pitch sheaves for motors 15 horsepower and under, selected so required rpm is obtained with sheaves set at mid-position.  Fixed sheave for 20 horsepower and over.  Where more than one belt is required, matched sets shall be used.  Include an additional set of drives for each fan to be used for final adjustments.  After correct speed has been determined with variable sheave, provide fixed sheaves.

EXECUTION

INSTALLATION

Installation shall meet or exceed all applicable federal, state and local requirements, referenced standards and conform to codes and ordinances of authorities having jurisdiction.

All installation shall be in accordance with manufacturer’s published recommendations.

Roof Curbs:  Roof curb installation shall be coordinated with Owner and Contractor.

Disconnect Switches:  Disconnect switches shall be installed adjacent to fan on unistrut per Division 26.  Coordinate installation with Owner.

PAINTING

Provide equipment with factory finish in accordance with the manufacturer's standards.  Touch up scratches and marks from handling and installation with masking enamel to match manufacturer's color.

Where exhaust fans are required to have Heresite coating, have units factory finished with required number of coats prior to shipping to the Project Site.

Refer to Division 09 for Site-applied finishes.

END OF SECTION 23 34 23