SECTION 23 37 00 – air outlets and inlets

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

Specifications throughout all Divisions of the Project Manual are directly applicable to this Section, and this Section is directly applicable to them.

SUMMARY

Perform all Work required to provide and install diffusers, diffuser boots, registers/grilles, louvers, louver penthouses, roof hoods, and goosenecks indicated by the Contract Documents with supplementary items necessary for proper installation.

REFERENCE STANDARDS

The latest published edition of a reference shall be applicable to this Project unless identified by a specific edition date.

All reference amendments adopted prior to the effective date of this Contract shall be applicable to this Project.

All materials, installation and workmanship shall comply with the applicable requirements and standards addressed within the following references:

AMCA 500 - Test Method for Louvers, Dampers and Shutters.

ANSI/NFPA 90A - Installation of Air Conditioning and Ventilating Systems.

ARI 890 – Rating of Air Diffusers and Air Diffuser Assemblies.

ASHRAE 70 - Method of Testing for Rating the Air Flow Performance of Outlets and Inlets.

SMACNA 1035 - HVAC Duct Construction Standards - Metal and Flexible.

QUALITY ASSURANCE

Test and rate performance of air outlets and inlets in accordance with ASHRAE 70.

Test and rate performance of louvers in accordance with AMCA 500.

SUBMITTALS

Product Data:

Submit product data and Shop Drawings, indicating type, size, location, application, noise level, finish, and type of mounting.

Review requirements of outlets and inlets as to size, finish, and type of mounting prior to submitting product data.

Operation and Maintenance Data:

Submit manufacturer’s installation instructions under provisions of Division 01.

PRODUCTS

GENERAL

All materials shall meet or exceed all applicable referenced standards, federal, state and local requirements, and conform to codes and ordinances of authorities having jurisdiction.

Grilles, registers and diffusers shall be as scheduled on the Drawings Grilles, registers and diffusers shall be provided with sponge rubber or soft felt gaskets where noted on the Drawings Grilles, slot diffusers and laminar flow bars shall not be internally insulated.  If a manufacturer other than the one scheduled is used, the sizes shown on the Drawings shall be checked for performance, noise level, face velocity, throw, pressure drop, etc., before the submittal is made.  Selections shall meet the manufacturer’s own published data for the above performance criteria.  The throw shall be such that the velocity at the end of the throw in the five (5) foot occupancy zone will not exceed 50 fpm nor be less than 25 fpm except where indicated otherwise.  Noise levels shall not exceed those published in ASHRAE for the type of space being served (NC level).  In the vicinity of lab hoods, terminal velocity at face of hood shall not exceed 20 fpm.

Locations of air distribution devices on Drawings are approximate and shall be coordinated with other trades to make symmetrical patterns and shall be influenced by the established general pattern of the lighting fixtures or architectural reflected ceiling plan, but primarily located to maintain proper air distribution.  Where called for on Drawings, grilles, registers and diffusers shall be provided with deflecting devices and manual dampers.  These grilles, registers, and diffusers shall be the standard product of the manufacturer, and subject to review by the Architect.

Provide a frame compatible with the type of ceiling or wall in which the devices are installed.  Refer to Architectural Drawings for exact type of ceiling specified.

Coordinate color and finish of the devices with the Architect.

manufacturers

Grilles, Registers, and Diffusers:

Krueger Manufacturing Company.

Titus Products.

Price Industries.

Nailor Industries.

Louvers:

American Warming and Ventilating.

Ruskin.

Greenheck.

Arrow.

Roof Hoods:

Greenheck.

Cook.

Acme.

ROUND CEILING DIFFUSERS

Round, adjustable pattern, stamped or spun, multicore type diffuser to discharge air in 360-degree pattern, with sector baffles where indicated.

Project diffuser collar above ceiling face and connect to duct with duct ring.  In plaster ceilings, provide plaster ring.

Fabricate of aluminum, unless otherwise noted, with factory baked enamel, off-white finish.

Provide multi-louvered equalizing grid where noted on Drawings.

RECTANGULAR CEILING DIFFUSERS

Rectangular, full louvered face, directional, removable multi-core type diffuser to discharge air in 360-degree pattern. Neck size shall be as scheduled on the Drawings.  Provide filler panels, where required, for directional throw diffusers.

Fabricate frame and blades of extruded aluminum with factory baked enamel, off-white finish.

Provide multi-louvered equalizing grid .where noted on Drawings

Provide round neck connection as scheduled on Drawings.

PERFORATED FACE CEILING DIFFUSERS

Perforated face with fully adjustable pattern and removable face.

Fabricate of aluminum with factory baked enamel, off-white finish.

Provide multi-louvered equalizing grid where noted on Drawings.

Provide round neck connection as scheduled on Drawings.

SQUARE PANEL FACE SUPPLY AND RETURN AIR CEILING DIFFUSER

Architectural diffuser with a square panel centered within a square housing similar to the Titus OMNI model.  Drawings that depict two-way and three-way throw options are achieved with the use of filler panel (where required) for directional throw diffusers.

Opposed blade volume dampers shall be provided with the diffuser, if scheduled on the Drawings.  The volume damper design shall be similar to the Titus AG-75.

Although the manufacturers show this model being used only as a supply air device, this same diffuser can also be used as a return air device.  The neck connection shall be the largest available neck size provided by the manufacturer.

Provide round neck connection as scheduled on Drawings.

CEILING EXHAUST AND RETURN REGISTERS/GRILLES

Streamlined blades, depth of which exceeds 3/4-inch spacing, with spring or other device to set blades, vertical face.

Fabricate 1-inch margin frame with concealed mounting.

Fabricate of steel with minimum 20 gage frames and minimum 22 gage blades, steel and aluminum with minimum 20 gage frame, or aluminum extrusions, with factory baked enamel finish.

Opposed blade damper with removable key operator, operable from face shall only be provided with the grille when it is scheduled on the Drawing.

PERFORATED FACE RETURN/EXHAUST GRILLES

Perforated face with back pan, removable face, and neck sizes as indicated on Drawings.

Provide frame type as indicated on Drawings.

Fabricate completely of 22 gage steel with a baked enamel off-white finish.

LIGHT TROFFER DIFFUSERS

Single plenum type constructed independent of light troffers with volume and pattern controllers with oval top or side air inlet as scheduled.

Match diffusers to light troffers and connect in airtight connection without tools.

Fabricate of galvanized steel with welded or soldered joints and finish matte black inside.

PERFORATED FACE CEILING EXHAUST AND RETURN REGISTERS/GRILLES.

0.0375-inch stainless steel non-aspirating perforated panels with stainless steel plenum for low-velocity applications.

Provide quick-opening fasteners with safety chains.

Provide multi-louvered equalizing grid where noted on Drawings.

CEILING EGG CRATE EXHAUST AND RETURN REGISTERS/GRILLES

Fixed series of cubes comprised of 1/2 x 1/2 x 1-inch aluminum strips.

Fabricate one-inch margin aluminum frame.

Fabricate of aluminum with factory baked enamel finish.

Provide square uniform height plenum for ducted return and exhaust application of scheduled neck size.

CEILING LINEAR SLOT DIFFUSERS

Continuous linear flow bar slot with adjustable vanes for left, right, or vertical discharge, with volume control. Provide slot width, length and number of slots as scheduled on the Drawings.

Fabricate of aluminum extrusions with factory baked enamel finish.

Provide support clips and gasket as required for ceiling system.

Provide alignment strips for hairline joints and end caps where the slot terminates. Provide mitered corners.

Provide black matte finish for all interior exposed-to-view components.

Provide externally insulated supply air plenum by diffuser manufacturer.

Provide return slot diffuser same as supply, except without the adjustable vane control. Provide return air plenum for ducted return where indicated on Drawings.

Plenum Slot Supply AND return Diffusers

Supply or return plenum slot, 3/4-inch, with single extruded aluminum curved deflector blade to create a tight horizontal airflow pattern across the ceiling.  Provide slot width, length, and number of slots as scheduled on the Drawings.

Diffusers shall discharge air horizontally through two outside sections and vertically through a center down-blow section.

Standard nominal lengths shall be 2, 3, 4, or 5 feet. Units shall be constructed of 24 gage steel. Maximum height of the unit’s plenum shall be 7-inches. Inlets shall have a minimum of 1-1/2-inch depth for duct connection. The standard finish shall be black on the face of the diffuser and pattern deflectors.

Diffuser shall be similar to Titus N-1-R diffuser.

PErimeter Slot Supply and Return Diffusers

High induction supply and return plenum slot, the supply is a 3/4-inch fixed slot width that produces a horizontal discharge pattern, and a return air slot with a maximum 1-1/2-inch slot width.  Provide length as scheduled on the Drawings.

Standard nominal lengths shall be 2, 3, 4, or 5 feet. Units shall be constructed of 24 gage steel. Maximum height of the units shall be 7-inches. Inlets shall have a minimum of 1-1/2-inch depth for duct connection. The standard finish shall be black on the face of the diffuser and pattern deflectors.

Diffuser shall be similar to the Titus N-1-R diffuser.

CEILING LINEAR EXHAUST AND RETURN GRILLES

Streamlined blades with 90-degree one-way deflection, 1/8-inch x 3/4-inch on 1/4-inch centers.

Fabricate 1-inch margin frame with countersunk screw mounting.

Fabricate of steel with 22 gage minimum frames and 22 gage minimum blades, steel and aluminum with 20 gage minimum frame, or aluminum extrusions, with factory baked enamel finish.

Opposed blade damper with removable key operator, operable from face shall only be provided with the grille when it is scheduled on the Drawing.

WALL SUPPLY REGISTERS/GRILLES

Streamlined and individually adjustable curved blades to discharge air along face of grille with two-way deflection.

Fabricate 1-inch margin frame with countersunk screw, concealed mounting and gasket.

Fabricate of aluminum extrusions with factory clear anodized finish.

Provide multi-louvered equalizing grid where noted on Drawings.

WALL EXHAUST AND RETURN REGISTERS/GRILLES

Streamlined blades, depth of which exceeds ¾-inch spacing, with spring or other device to set blades, vertical or horizontal face as scheduled.

Fabricate one-inch margin frame with concealed mounting.

Fabricate of aluminum with 20 gage minimum frame, or aluminum extrusions, with factory baked enamel finish.

LINEAR BAR WALL DIFFUSERS

Streamlined blades with 0 to 15 degree deflection, as scheduled, 1/8-inch x 3/4-inch or 1/4-inch centers.

Fabricate of aluminum extrusions, with factory clear anodized finish.

Fabricate 1/2-inch margin frame with concealed mounting and gasket.

Provide concealed fastening, straightening grids and alignment bars.

Provide externally insulated plenums by diffuser manufacturer.

Provide return bar diffusers same as supply with return air plenum.

Silhouette finish.

LINEAR FLOOR SUPPLY REGISTERS/GRILLES

Streamlined blades with zero degree deflection, 7/32-inch x 3/4-inch on 1/2-inch centers.

Fabricate of high-grade aluminum extrusions with factory clear anodized finish.

Fabricate 3/16-inch margin heavy margin frame with concealed mounting and gasket and mounting frame.  Frameless flange for floor installation.  Silhouette finish.

Provide concealed fastening, straightening grids and alignment bars.

LABORATORY RADIAL AIR SUPPLY DIFFUSERS

High-volume, low velocity performance.

Diffuser shall provide non-aspirating radial air pattern and shall be configured with air supply plenums with inlet collars to assure uniform velocity over the diffuser face.

Furnish stainless steel back pan and stainless steel faced diffusers for animal holding rooms.

Furnish aluminum back pan and aluminum-faced diffusers for laboratories.

Performance face drops below ceiling, single-pane back pan and single piece lower chamber.  Sectioned diffuser is not acceptable.

WALL EXHAUST AND RETURN REGISTERS/GRILLES – SEVERE DUTY

Streamlined 40-degree fixed blades, at 1/2-inch spacing, with horizontal front blades.

Fabricate 1-1/4-inch margin frame with vandal-proof screws.

Fabricate totally of steel with minimum 18 gage frames and minimum 14 gage blades with factory baked enamel finish.

DOOR GRILLES

V-shaped louvers of 20 gage steel, 1-inch deep on 1/2-inch centers.

Provide 20 gage steel frame with auxiliary frame to give finished appearance on both sides of door, with factory prime coat finish.

LOUVERS

Provide 6-inch deep louvers with blades on 45-degree slope with center baffle and return bend, heavy channel frame, birdscreen on interior side with 1/2-inch square mesh for exhaust and 3/4-inch for intake.

Fabricate of 12 gage extruded aluminum, welded assembly, with factory prime coat finish.

Furnish with exterior angle flange for installation.

Fabricate louver penthouses with mitered corners and reinforce with structural angles.

Pass 750 feet per minute free velocity with less than 0.10 inches of water pressure drop, based in accordance with AMCA 500.  Water penetration less than 0.025 ounce of water per foot of free area at 900 feet per minute.  Provide a minimum of 45 percent free area.

ROOF HOODS

Fabricate air inlet or exhaust hoods in accordance with SMACNA 1035, 1-inch classification Duct Construction Standards.

Fabricate of galvanized steel, minimum 16 gage base and 20 gage hood, or aluminum, minimum 16 gage base and 18 gage hood; suitably reinforced; with removable hood; birdscreen with 1/2-inch square mesh for exhaust and 3/4-inch for intake, and factory prime coat finish.

Roof curb shall be coordinated with Owner and roofing Contractor.

Hood outlet area shall be minimum two times the throat area.

GOOSENECKS

Fabricate in accordance with SMACNA 1035, 1-inch classification, of minimum 18 gage galvanized steel.

Roof curb shall be coordinated with Owner and roofing Contractor.

EXECUTION

INSTALLATION

Installation shall meet or exceed all applicable federal, state and local requirements, referenced standards and conform to codes and ordinances of authorities having jurisdiction.

All installation shall be in accordance with manufacturer’s published recommendations.

Check location of air outlets and inlets and make necessary adjustments in position to conform to architectural features, reflected ceiling plans, symmetry, and lighting arrangement.

Install air outlets and inlets to ductwork with airtight connection.

Provide balancing dampers on duct take-off to diffusers, grilles and registers, regardless of whether dampers are specified as part of the diffuser, grille, or register assembly.  The use of extractors or scoops at duct take-off to diffusers, grilles and registers is not allowed.

Paint ductwork visible behind air outlets and inlets matte black. Refer to Division 09.

Provide all specialties and frames for air distribution devices as required for proper installation in ceiling type as indicated on Architectural Drawings.  Provide all cutting and patching of T-bars, gypsum board, and other ceiling systems as required for installation of air devices.

END OF SECTION 23 37 00