SECTION 23 57 20 – plate and frame heat exchangers

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

Specifications throughout all Divisions of the Project Manual are directly applicable to this Section, and this Section is directly applicable to them.

SUMMARY

Perform all Work required to provide and install plate and frame heat exchangers, accessories and trim indicated by the Contract Documents with supplementary items necessary for proper installation and operation.

REFERENCE STANDARDS

The latest published edition of a reference shall be applicable to this Project unless identified by a specific edition date.

All reference amendments adopted prior to the effective date of this Contract shall be applicable to this Project.

All materials, installation and workmanship shall comply with the applicable requirements and standards addressed within all references.

QUALITY ASSURANCE

The complete assembly shall be factory assembled and tested in accordance with ASME Code, Section VIII, Division I, and furnished with ASME Code Certification (VI Form) for design pressures as specified in this Section.

SUBMITTALS

Product Data and Record Documents:

Submit Shop Drawings and product data for manufactured products and assemblies.

Indicate empty and operating weights, frame length, height, plate width, and clearance dimension requirements, locations and size and rating of flanged connections.  Provide certified performance data heat exchanger hot and cold inlet and outlet water temperatures, flow rates, the design approach temperature, the pressure differential at the design flow rates as shown on the Drawings.

Submit design, manufacturing and material data in sufficient detail to verify that heat exchangers meet or exceed specification requirements.

Submit test reports of heat exchanger pressure tests.

Submit manufacturer's operating maintenance and installation (IOM) instructions including recommended insulation type, thickness and jacket material.

Submit samples of plates, gaskets and nuts and bolting materials for each heat exchanger size.

Operation and Maintenance Data:

At Substantial Completion, the contractor shall submit operation and maintenance data that includes Start-up and shutdown instructions, assembly Drawings, and recommended spare parts lists from the manufacturer.

DELIVERY, STORAGE and HANDLING

Deliver, store, protect and handle products to the Project Site under provisions of Division 01 and Division 20.

Protect internals from entry of foreign material by temporary caps on flanged openings.

PRODUCTS

GENERAL

All materials shall meet or exceed all applicable referenced standards, federal, state and local requirements, and conform to codes and ordinances of authorities having jurisdiction.

Furnish and install plate and frame heat exchangers designed with manufacturer's standard fouling allowance and guaranteed to perform to the capacities and pressure drops at the fluid temperatures and flow rates as scheduled.

Units shall be pressure rated for 150 psig cold (distribution system side) and 300 psig hot (building side).

manufacturers

APV Crepaco, Inc.

Tranter PHE, Inc.

ITT Bell & Gossett.

Alfa – Laval, Inc.

Paul Mueller Company (Accu-Therm).

Frames

Provide carbon steel frames, cleaned of mill scale, primed and painted with two (2) coats of baked epoxy enamel.

Provide a minimum of two (2) lifting lugs per frame, designed for lifting assembled flooded unit.

Plates

Provide Type 316 stainless steel heat transfer plates with herringbone corrugations designed to provide support to adjacent plates to allow pressurization of each circuit to a full differential of 1.5 times the design working pressures without deformation.

All ferrous materials in contact with fluids on the hot and cold sides shall be Type 316 stainless steel.

Overall plate area should be increased by 10% to account for fouling that will occur as the heat exchanger is being used.

Heat transfer plates shall include tapered gasket grooves and shall receive standard IIB finish.

Each heat transfer plate shall have a glued one-piece nitrile-butadiene molded gasket with relieving grooves to prevent mixing of fluids and to divert leakage to outside of unit.

Provide OSHA compliant aluminum splashguard over channel plate rack and shroud around plate pack.

Nozzles

Provide flanged nozzles (sized as shown on Drawings) on end frames designed for system working pressures as specified.  Nozzle velocities shall not exceed 10 fps at the maximum rate of heat transfer as scheduled on the Drawings.

Bolts

Compression bolts shall be cadmium plates and shall be coated with molybdenum grease for rust protection.  Provide plastic sleeve to protect bolts.

Bolts shall be provided with rolled threads to reduce galling and double-width hex nuts to distribute the load.

Nameplates

Each exchanger shall have a stainless steel nameplate permanently attached to the frame.  The nameplate shall be mounted off the surface of the heat exchanger to permit the application of 2-inch thick insulation.

Nameplate brackets shall be fabricated from thermally nonconductive materials to eliminate sweating.

The nameplate shall include as a minimum, the following data stamped on the face of the nameplate:

Project name.

Customer order number.

Equipment designation.

Year manufactured.

Hot and cold side design.

Temperatures.

Working pressures.

Design flow rates.

Pressure differentials at design flow rates.

All information required for plate pack compression.

Model and serial numbers.

EXECUTION

INSTALLATION

Installation shall meet or exceed all applicable federal, state and local requirements, referenced standards and conform to codes and ordinances of authorities having jurisdiction.

All installation shall be in accordance with manufacturer’s published IOM and recommendations.

Install to permit disassembly of plate pack with minimum disturbance to piping and equipment.

Support heat exchangers on 6-inch housekeeping pads.

Pipe relief valves to nearest floor drains.

Pipe drain and vent valves to nearest floor drain.

Fabricate and install a galvanized steel drip pan with a 1-inch drain pipe routed to the nearest equipment floor drain.  The dimensions of the drip pan shall be wide and long enough to capture a fluid leak coming from the plate pack.

Provide thermometers, wells and temperature and pressure indicating gauges in supply and return piping at the hot and cold side connections of the exchanger.

Insulate the heat exchanger frame and plate shroud as required to prevent condensation on cold surfaces.

END OF SECTION 23 57 20