SECTION 26 36 23 – automatic transfer switches

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

Specifications throughout all Divisions of the Project Manual are directly applicable to this Section, and this Section is directly applicable to them.

SUMMARY

This Section specifies the furnishing and installation of automatic transfer switches. Where indicated on the Drawings, switches are to have integral isolation/bypass switches

REFERENCE STANDARDS

The latest published edition of a reference shall be applicable to this Project unless identified by a specific edition date.

All reference amendments adopted prior to the effective date of this Contract shall be applicable to this Project.

All materials, installation and workmanship shall comply with the applicable requirements and standards addressed within the following references:

ANSI/UL 1008 - Automatic Transfer Switches.

NEMA ICS 1-109 - Tests.

NEMA ICS 2-447 - A-C Automatic Transfer Panels.

NFPA 20 - Standard for Centrifugal Fire Pumps (for switches utilized with fire pumps).

NFPA 70 - National Electrical Code.

NFPA 99 - Essential Electrical Systems for Health Care Facilities.

NFPA 110 - Standard for Emergency and Standby Power Systems.

IEEE 446 - IEEE Recommended Practice for Emergency and Standby Power -Systems.

IEEE 241 - IEEE Recommended Practice for Electrical Power Systems in Commercial Buildings.

SUBMITTALS

Product Data and Record Documents:

Include the following information in the submittal:

Rated current, voltage and frequency.

Number of poles.

UL 1008 3-cycle close and withstand rating.

Physical dimensions.

NEMA enclosure type.

Itemized list of accessories.

Schematic diagram (show wiring and only those components which are part of switch).

Show all factory wiring on wiring diagram and clearly indicate all wiring and connections to remote devices which are to be made in the field.  (Show only that wiring which pertains to switch and remote devices.)

Indicate control wiring for communications package.

PRODUCTS

GENERAL

All materials shall meet or exceed all applicable referenced standards, federal, state and local requirements, and conform to codes and ordinances of authorities having jurisdiction.

Provide a switch which is electrically operated and mechanically held in each direction, and which is true double-throw with Isolation bypass (closed transition).

Provide automatic transfer switches (ATS) with number of poles, voltage and current ratings as shown on the Drawings.

Each ATS shall consist of an inherently double-throw power transfer switch unit and a control module interconnected to provide complete automatic operation.

Provide a microprocessor control panel.

MANUFACTURERS

The ATS manufacturer shall maintain a local service center capable of emergency service or routine preventive maintenance and shall offer preventive maintenance contracts.

Manufacturers:

ASCO.

Construction

The transfer switch unit shall be electrically operated and mechanically held.

The electrical operator shall either be a single or dual motor design with over-center type linkage solenoid mechanism, momentarily energized to minimize power consumption and heat generation.

The switch shall be positively locked and unaffected by voltage variations or momentary outages so that contact pressure is maintained at a constant value and temperature rise at the contacts is minimized for maximum reliability and operating life.

The switch shall be mechanically interlocked to ensure only one of two possible positions - normal or emergency for single solenoid design and three possible positions - normal off, emergency for dual motor design.

All main contacts shall be silver-plated copper composition.  All switches shall have segmented, blow-on construction for high withstand current capability and be protected by separate arcing contacts.

ATS utilizing components of molded-case circuit breakers, contactors or parts thereof which have not been intended for continuous duty, repetitive switching or transfer between two active power sources are not acceptable.

Inspection of all contacts (movable and stationary) shall be possible from the front of the switch without disassembly of operating linkages and without disconnection of power conductors. An insulated manual operating handle shall be provided for maintenance purposes.

Utilize quick-make quick-break contacts mounted so that contact position may be verified by observation.

All terminal lugs shall be compression, AL/CU Type.

All neutral conductors shall be connected solidly with a fully-rated AL/CU compression connection.

Operation

The voltage of each phase of the normal source shall be monitored, with pickup adjustable from 85 to 100 percent and dropout adjustable from 75 to 98 percent of pickup setting, both in increments of 1 percent, and shall be fully field-adjustable.  Repetitive accuracy of settings shall be + 2 percent or better over an operating temperature range of -20 degrees C to 70 degrees C.  Factory set to pick up at 90 percent and drop out at 85 percent.

Single-phase voltage sensing of the emergency source shall be provided, with a pickup adjustable from 85 to 100 percent (and dropout fixed at 84 to 86 percent of pickup), and frequency sensing with pickup adjustable from 90 to 100 percent (and dropout fixed at 87 to 89 percent of pickup).  Both pickup settings shall be fully field adjustable.  Repetitive accuracy of settings shall be ( 2 percent or better over an operating temperature range of -20 degrees C to 70 degrees C.  Factory set to pick up at 90 percent voltage and 95 percent frequency.

The control module shall include four (4) time delays that are fully field adjustable in increments of at least 13 steps over the entire range as follows:

Time delay to override momentary normal source outages to delay all transfer switch and engine starting signals.  Adjustable from 0 to 6 seconds.  Factory set at 1 second.

Transfer to emergency time delay.  Adjustable from 0 to 5 minutes.  Factory set at 0 minutes, unless indicated otherwise on the Drawings.

Retransfer to normal time delay.  Time delay is automatically bypassed if emergency source fails and normal source is acceptable.  Adjustable from 0 to 30 minutes.  Factory set at 30 minutes.

Unloaded running time delay for emergency engine generator cool-down. Adjustable from 0 to 60 minutes.  Factory set at 0 minutes.

A set of DPDT silver composition contacts rated 10 amps, 32 VDC shall be provided for a low-voltage engine start signal when the normal source fails.  The start signal shall prevent dry cranking of the generator by requiring the generator to reach proper output, and to run for the duration of the cool-down setting, regardless of whether the normal source restores before the load is transferred.

Provide a pushbutton to bypass time delay on retransfer to normal.

A momentary-type test switch shall be provided to simulate a normal source failure.

Output terminals to signal the actual availability of the normal and emergency sources, as determined by the voltage-sensing pickup and dropout settings for each source, shall be provided.

Provide the following sets of dry auxiliary contacts rated 10 amps 480 VAC wired to an accessible terminal strip. Building automation system (BAS) Provider shall connect these contacts to the BAS for remote monitoring:

One (1) contact closed when the ATS is connected to normal;

One (1) contact closed when the ATS is connected to emergency;

One (1) contact closed when the normal power is available; and

One (1) contact closed when emergency power is available.

It is unacceptable to have one (1) form C contact to account for more than one of the specified auxiliary contacts.

Provide four (4) sets of signal lights to indicate the following:

When the ATS is connected to normal source;

When the ATS is connected to emergency source;

When normal power is available; and

When emergency power is available.

Form C contacts are unacceptable.  Contacts shall be wired to an accessible terminal strip.

Each switch shall be furnished with an operator's manual providing installation and operating instructions.

On all switches not part of a bypass isolation switch assembly, provide an external emergency manual operator, UL listed for transferring the switch to either source under load.

Provide LED type indicating lights; one to indicate normal power (green), one to indicate emergency (red).  Provide indicating lights for both normal and emergency availability.

Bypass/Isolation Operation:

Provide a bypass/isolation switch to electrically bypass and isolate each automatic transfer switch.  The switch must be capable of bypassing to whichever source the ATS is connected to.

The bypass/isolation switch also permits continuous service in case the transfer switch is inoperable, damaged, or removed.

All auxiliary circuits to the automatic transfer switch remain in service during operation of the bypass/isolation switch.  Interlocking shall be provided to prohibit personnel from controlling the sequence of operations and to prevent operation to the isolation position until the bypass function has been completed.

Inphase Monitor:

If the ATS is of a single solenoid design, an inphase monitor shall be built-in to the ATS and shall control transfer so that motor load inrush currents do not exceed normal starting currents, to avoid nuisance tripping of circuit breakers and possible mechanical damage to motor couplings.

The inphase monitor shall operate without external control of electrical loads and without any external control of the power sources.

The monitor shall compare the phase relationship and frequency difference between the normal and emergency sources and permit transfer the first time the sources are within 15 electrical degrees and only if transfer can be accomplished within 60 electrical degrees as determined by monitoring the frequency difference.

lnphase transfer shall be accomplished if both sources are within 2 Hz of nominal frequency and 70 percent or more of nominal voltage.  This is not required for dual motor design.

Center Off Position:  If the ATS is of the dual motor design, a time delay relay shall be provided to vary the center off delay from 0 to 60 seconds.

Provide an elevator pre-signal before transfer to Normal after operating on Emergency during an outage.  Provide pre-signal for testing and for switching during transfer between energized sources.

MAIN CONTACT PROTECTION AND WITHSTAND CURRENT RATINGS

Protect main contacts by providing arc barriers on each contact, and on switches rated above 300 amperes by providing separate arcing contacts.

The ATS shall be UL 1008 listed for a 3-cycle close and withstand current rating as indicated on the Drawings.  Series rating of switches with particular circuit breakers or fuses is not acceptable.

NEUTRAL BAR

Provide a 100 percent rated neutral bar with the same capacity as the ampere rating of the switch, unless otherwise noted on the Drawings.

ENCLOSURE

Provide NEMA 1 switch enclosure suitable for wall or floor mounting.

Mount the bypass/isolation switch in a common enclosure with the associated transfer switch. Separate the bypass/isolation switch from the associated transfer switch by a metal divider panel.

Make the switch operable from a dead-front location.  Design switch so that it can be padlocked in the bypass/isolation position.

Permanently attach wiring diagrams and maintenance instructions on the inside of enclosure door in a mounting designed to hold the data.  Instructions shall be laminated.

EXECUTION

INSTALLATION

Installation shall meet or exceed all applicable federal, state and local requirements, referenced standards and conform to codes and ordinances of authorities having jurisdiction.

All installation shall be in accordance with manufacturer’s published recommendations.

Install the automatic transfer switches as shown on the Drawings.

Painting:  Restore any marred surfaces to factory finish.

TESTING

Test the switches with the packaged electric generator set in operating condition.

Demonstrate to the Owner that the automatic transfer switches and bypass isolation switches perform all required functions.

Training

Formal training for the operation and maintenance of all equipment and systems specified herein shall be given by factory trained and certified personnel.

Training shall consist of a minimum of two, complete 4-hour training sessions.

Timing of the training should coincide with the schedule for the manufacturer's representatives to be on Site for testing and Start-up of the systems.

The specified training shall be given at a location designated and provided by the Owner for a minimum of ten (10) personnel selected by the Owner, in addition to any necessary on-Site orientation and training.

A training program shall be submitted with material, instructors' qualifications, and proposed schedule, a minimum of 60 days prior to the proposed training.

The Owner reserves the right of approval of any training course, material, instructor and schedule.

END OF SECTION 26 36 23