&

Standards Document

# Table of Contents

Table of Contents	2

Controller requirements	5

BJC Requirements	6

BJC IT Standards	7

Installing OR Upgrading MSEA	8

System Layout	9

Construction Server	10

Site Names & Abbreviations	11

Engine Names	12

Naming unique items	13

Designated Site Number	14

BACnet Object Identifiers	15

NAE BACnet Object Identifier	16

Trunk BACNOID Object Identifier	17

Field Bus Name	18

Field Device Name	19

Field Object Name	20

Item Organization	21

Assign Custom Categories to Items	23

User Views	24

Offline Server	25

Software Changes	26

Alarm Management	27

Email and Paging	30

Trending	31

Other Topics:	32

Controls Standards	33

Graphics	34

Appendix A: Assigned Categories	39

Appendix B: BJC- BACnet Network Tracking Worksheet v.1.1	42

Appendix C: Database Generation Checklist	43

Appendix F: Process Flow Maps	45

Preface

This manual is to be used as a guideline to ensure all additions to the Metasys BAS Network and Database follow a consistent standard that has been previously established by JCI. The Database Generation Checklist provided in Appendix C is to be followed when building a database for all devices on the BJC Healthcare Metasys Network.

# Controller requirements

- The Control Device hardware with a display on the local device is required when available

- Labels for the equipment the device is controlling is required (Not Pictured).

Label here

- The Supervisory Controllers with a display on the local device is required when available

- Labels with the Device Name and IP address is required (Not pictured).

Label here

# BJC Requirements

- Chilled Water Valve Operation and Economizer Damper Operation will operate independently of each other. All units will have the ability to economize and open the chill water valve at the same time.

- Preheat Valves will modulate to maintain discharge air temperature when in normal operation.

- Schedules will not include more than one major piece of equipment.

- Point to point checkout is required before a project will be considered substantially completed.

- Graphics will be included/updated for all equipment with every project.

- All LCT programming and related objects will be kept in NAE in folders below the Programming Folder based on System Name.

- NAE Power Sampling Intervals will be set at 30 seconds

- No Supervisory Device unbound references allowed at project completion

- No offline Controllers are allowed at Project completion in all items

- New Engines will be added to the server SCT Database when directed to the Production Server

# BJC IT Standards

Electronic devices that need an IP address must have a dedicated drop ran from the BJC Network access point to each device.

If the guest wireless signal is not available at the engine or equipment location, a wireless Network Access Point must also be requested.

IP addresses should be requested when network access point drops are requested.

Absolutely no unapproved network access point (switch/hub) should be connected to the BJC network at any time.

All Technicians will use the guest wireless signal while at BJC HSO Facilities, and log into SecureLink to connect to the BJC Network the when connecting to the Metasys BAS Network.

# Installing OR Upgrading MSEA

Steps to take before upgrading the Metasys Application on the server:

The NXE Supervisory devices are constantly forwarding data to the server. If the Server is going to be down for maintenance, the data samples should be routed to the server in an attempt to prevent gaps in the data being collected.

- Copy the upgrade program files to the ADX.

- Server and Database Administrative rights are required to perform a software upgrade by the user logged into the server. The BJC Application Support Team should be on a conference call during the upgrade for support. Prior to an upgrade, a temporary Database Administrative Access Request is needed, which can be obtained through a service now request. A temporary window can only be approved for Database Administrative rights for users that are already assigned Server Administrative Rights.

# System Layout

The example below provides the location to the items referenced within this document

Note: The names in the screenshots for the archive are for reference only and do not reflect the actual names.

# Construction Server

New Engines will be reporting to the Construction Server Prior to being pointed at the Central Server. The BJC Remote Operations Center Manager will approve the setup of all engines prior to being directed to the BJC BAS Production Server.

Site

BACnet Site

# Site Names & Abbreviations

To get the various Metasys objects named correctly use the Site Abbreviation in the table below for the object prefix.

| Abbreviation | Site |
| --- | --- |
| BJH | Barnes Jewish Hospital |
| SLCH | St. Louis Children’s Hospital |
| MBMC | Missouri Baptist Medical Center |
| AMH | Alton Memorial Hospital |
| BJSP | Barnes-Jewish St. Peters |
| PWH | Progress West Hospital |
| PHC | Parkland Health Center |
| CNE | Christian North East |
| CNW | Christian North West |
| COM | BJC Commons |
| PDC | Primary Data Center |
| CSCC | Children’s Specialty Care Clinic |
| BJHEC | Barnes-Jewish Hospital Extended Care |
| SSC | Siteman South County |
| MBH | Memorial Hospital Belleville |
| MHE | Memorial Hospital East (Shilo) |

# Engine Names

The engine name must contain the site prefix and the next consecutive engine number for that site with a description. This description should help to locate the engine if it is offline.

Engine Names

- See Site Names & Abbreviations table for correct prefix

- Engine name = Site + NAE Type + ##

- Number increment starts at 01 for each Site

- Description = Room Location of NAE / System(s) Served

# Naming unique items

The user views and folders under the server need to be named unique to the site you are working on.

In the SCT Archive for the Construction Server the user views and folders under the server need to be named unique to the site you are working on, unless they can be used for multiple sites. See Site Names & Abbreviations table for correct prefix.

# Designated Site Number

The Engines and Trunks need a unique Bacnet Object Identifier and those numbers will start with the Bacnet ID Site Number as indicated below.

| Site Number | Site Name |
| --- | --- |
| 01 | BJH (Barnes Jewish Hospital) |
| 02 | SLCH (St. Louis Children’s Hospital) |
| 03 | MBMC (Missouri Baptist Medical Center) |
| 04 | AMH (Alton Memorial Hospital) |
| 05 | BJSP (Barnes-Jewish St Peters) |
| 06 | PWH ( Progress West Hospital) |
| 07 | PHC (Parkland) |
| 08 | CNE (Christian North East) |
| 09 | CNW (Christian North West) |
| 10 | COM (BJC Commons) |
| 11 | PDC (Primary Data Center) |
| 12 | CSCC (Children’s Specialty Care Clinic) |
| 13 | Available |
| 14 | SSC (Siteman South County) |
| 15 | MHB (Memorial Hospital Belleville) |
| 16 | MHE (Memorial Hospital East) |
| 17 | Available |
| 18 | Available |
| 19 | Available |
| 20 | Available |
| 21 | BJH (Barnes Jewish Hospital) |
| 22 | BJH (Barnes Jewish Hospital) |
| 23 | BJH (Barnes Jewish Hospital) |
| 24 | BJH (Barnes Jewish Hospital) |
| 25 | BJH (Barnes Jewish Hospital) |

# BACnet Object Identifiers

Engine BACnet Object Identifiers shall consist of at least 4 numbers: the first two numbers represent the site category and the second two numbers represent the engine number.

NAE BACnet ID # = Site Facility Category # and NAE #

Example: For engine MBMC-NAE03 the BACnet ID is 0303

Engine Trunk BACnet Object Identifiers shall consist of 6 numbers: the first two numbers represent the site category, the second two numbers represent the engine number and the last two numbers represent the trunk.

Trunk Bacnet # = Site Facility Category # and NAE # and trunk #

Example: For engine MBMC-NAE03 trunk 2 the BACnet ID is 030302

# NAE BACnet Object Identifier

A unique Bacnet Object Identifier is needed for each engine in order to provide reliable communication across the network:

The NAE BACnet Object Identifier for each NAE should be set up as indicated previously.

# Trunk BACNOID Object Identifier

A unique Bacnet Object Identifier is also needed for each engine trunk in order to provide reliable communication across the network:

The NAE Trunk BACnet Object Identifier should be set up as indicated for each Trunk as previously indicated.

# Field Bus Name

- N2-x for N2 Trunk

- FC-x for MS/TP Field Bus

- Description includes NAE name

“N2-A”  “xxx N2 Trunk A”

“FC-A”   “xxx MSTP Field Bus 1”

“FC-B”   “xxx MSTP Field Bus 2”

“BACnet” “BACnet Field Bus”

“LON” “LON Field Bus”

“ModbusRTU” “Modbus RTU Field Bus”

“ModbusTCP” “Modbus TCP Field Bus”

# Field Device Name

- The Object Name of a controller will have the name of the system that the controller is serving

- The Object ID of each controller should use the following formula =

Engine # + Trunk Name (A or B) + 3-digit Address + 3-digit Controller Type

Trunk Name

Engine #

Address

Controller Types

FAC = FAC Controller

FEC = FEC Controller

VMA = VAV Modular Actuator

VND = Vendor Devices

01A004VMA

- The description of each controller should use the following formula =

Room or System Served + Equipment ID

- Software file name for controller application should match the controller’s Object Name

- Subdirectory structure on ADX for files should match the structure of the All Items Tree

# Field Object Name

Using unique object names as indicated will help the user to locate objects and provide consistency across the BJC Metasys Network. Following the same naming convention for objects will allow for better use of Metasys Summary Definition feature.

- Object ID should follow the Johnson Controls CCT (Controller Configuration Tool) software standard

- Object Names are the Johnson Controls CCT (Controller Configuration Tool) software standard naming convention and descriptions

- All object names need to maintain consistency relative to similar objects types

e.g. PRE-FILT vs P-FLT vs PREFILTER  = PFILT-S

- All NAE software objects (AV, BV, MV, MCO, etc) should follow the Johnson Controls CCT (Controller Configuration Tool) software standard naming

Object Names will not be modified from the Item Reference Name used during database generation.

# Item Organization

Graphic of Equipment

Graphics will be organized the same for each location and will be found under the server.

Trend Studies will be organized the same for each location and will be found under the server.

Items should be organized in a logical order and the same for each location. This will ensure that objects can be located quickly and efficiently every time a user attempts to locate that object.

# Assign Custom Categories to Items

All objects must be assigned the correct Custom Category

See Appendix A for Currently Assigned Site Categories

# User Views

- User Views will be created based on what is existing, and Tailored Summaries will be added

- In the absence of customer input, User Views will be created based on Building + Systems

- Tailored Summaries will be created for each piece of terminal equipment

- Any special User Views that need to be created must be identified in advance of database generation.

# Offline Server

If the Server is offline for an extended period of time, there is another way to view the critical equipment at the facilities. This is essentially a backdoor and should only be used by qualified personnel. These individuals can use the IP address of the engine to look into each engine and monitor critical equipment. It should be noted there will be no graphics, alarms, pages, and many options normally used while the server is down.

The logon screen will appear for the engine as pictured above. This login ID will be different than the login that users use to log into the server.

# Software Changes

All device software files shall be uploaded before any changes/adjustments are made in software configuration.

# Alarm Management

Alarms are used to notify people about facility problems and help direct the staff to what equipment needs attention.

- The following priority scheme will be used for alarms

Alarm Group		70

Warning Group		120

Normal Group		200

- Delays for Warning and Alarm for non-critical equipment, will follow this standard:

Report Delay = 15 minutes

Reference Delay Time = 30 minutes

- Alarm Message Text will be added for all critical alarms to identify system and location of object.  Customer to identify which alarms are critical.

- Alarm Message = Building + Mechanical System or Terminal Equipment Location + Alarm Message Text

“EW AHU-01 Air Handling Unit Failure Alarm”

“EW AHU-01 Room 111 High Temperature”

- Color schemes for alarm pop ups and event viewer

Scheme 1  		0 - 39		Red

Scheme 2  		40 -79		Red

Scheme 3		80 - 139	Yellow

Scheme 4		140 - 255	Yellow

- Naming Convention will use standards as described previously and Alarm Message Text to provide identification of equipment location for Alarms.  The “System Name.Object Name” convention is required to avoid the issue shown by the yellow arrow.

- This will also help in usability of the Event Viewer

# Email and Paging

The Custom categories for the site the email/pager is set up for must have the correct category assigned to the filter. If this is not added to the filter, then the email/pages for all locations will be sent to the email/pager destination that is added.

- Email routing should be determined by Alarm Priority,  Object Category,  Object Status and Time of Day

| Name | Filters |
| --- | --- |
| High Priority Day Time | Alarm Priority < 40 Object Category = PWH MAIN Object Status = Alarm Time of Day = 8am to 5pm Destination = john.doe@abc.com |

# Trending

- All Critical Systems – 15 min sample time, ADX repository = Enabled, Trend Buffer = 48

- All Mechanical Systems = 15 min sample time, ADX repository = Enabled, Trend Buffer = 48.  Includes all primary temperatures, pressures, flows, set points, valves and fan outputs

- All Zone Temperatures and Set Points = 30 min sample time, ADX repository = Disabled, Trend Buffer = 48

- Trending will be setup based on COV or Interval, whichever will minimize the data collected

- Trend Studies will be generated for all critical systems as defined by customer.

# Other Topics:

- When a NAE is added to the site, a new Security database containing both one administrator and one operator level user only shall be loaded into the controller.

- When an NAE is added to the site, that engine will also be added to the server SCT archive

# Controls Standards

This section is dedicated to Energy Savings Control Standards to be followed as applicable to the equipment selected. The reset should be done the same way each time to make it simpler and quicker on personnel to adjust and troubleshoot. All inputs and outputs should be exposed and adjustable.

1. Glycol Chiller Lockout Based Off of Cooling Valve Position

2. AHU Discharge Air Temperature Setpoint Reset Based on Outdoor Air Temperature

3. Discharge Air Static Pressure Setpoint Reset based On Zone Demand

4. Hot Water System Temperature Setpoint Reset Based on Outside Air Temperature

5. Heating Hot Water Pressure Reset based on Critical Valve Position

6. Condenser Water Temperature Setpoint Reset Schedule Based on Outside Air Temperature

The condenser water supply temperature setpoint is reset based on the outside air wet bulb temperature. The condenser water temperature setpoint will be the outside air wet bulb temperature plus 6 deg F.

For York chillers, the setpoint low limit will be 50 deg F and the setpoint high limit will be 78 deg F.

For Trane chillers, the setpoint low limit will be 65 deg F and the setpoint high limit will be 78 deg F.

7. Chilled Water Pressure Reset Based on Critical Valve Position

# Graphics

A graphical representation of the equipment the Building Automation System is controlling should be included with every controls project. The graphics should link all systems that are necessary to control an area with a hotlink button, if that system is on the BAS Network. This will make troubleshooting easier with all the systems associated with one another are linked together.

The following will be created as indicated in the BJC Graphics Plus Manual

- One graphic per major mechanical system

- Any additional graphics will be defined in advance of database generation

- The Graphics Plus environment will be used for creating the graphics

- Graphics to be created will be reviewed after partial (25%) completion for customer approval and sign off

- The following default color scheme will be used for object values shown on the graphics

The above graphic will be part of the Legend Graphic for each Campus.

These graphics must be consistent from one site to the next and should include the following:

1. Campus Page – This page will contain the various different buildings on the campus and have hot links to those buildings

2. Main Page/Dashboard – This page will contain the various different main systems within the building

3. AHU Selection Page – This contains all the AHUs for the building as a quick reference guide

4. Critical Room Monitoring Page – This page contains the important OR Data as a quick Reference guide and should be linked to the AHU for the Areas with a button. The room vavs should also be linked by clicking on the name of the room.

# Appendix A: Assigned Categories

| CATEGORY | ASSIGNED SITE | IN USE |
| --- | --- | --- |
| Custom 1 | SLCH MAIN |  |
| Custom 2 | SLCH |  |
| Custom 3 | SLCH |  |
| Custom 4 | SLCH |  |
| Custom 5 | SLCH |  |
| Custom 6 | SLCH |  |
| Custom 7 | SLCH |  |
| Custom 8 | SLCH |  |
| Custom 9 | SLCH |  |
| Custom 10 | SLCH |  |
| Custom 11 | SLCH |  |
| Custom 12 | SLCH |  |
| Custom 13 | SLCH |  |
| Custom 14 | SLCH |  |
| Custom 15 | SLCH |  |
| Custom 16 | SLCH |  |
| Custom 17 | SLCH |  |
| Custom 18 | SLCH |  |
| Custom 19 | SLCH |  |
| Custom 20 | SLCH |  |
| Custom 21 | PWH MAIN | X |
| Custom 22 | PWH MOB | X |
| Custom 23 | PWH |  |
| Custom 24 | PWH |  |
| Custom 25 | PWH |  |
| Custom 26 | COM MAIN | X |
| Custom 27 | COM |  |
| Custom 28 | COM |  |
| Custom 29 | COM |  |
| Custom 30 | COM |  |
| Custom 31 | BJSP MAIN | X |
| Custom 32 | BJSP MOB | X |
| Custom 33 | STP |  |
| Custom 34 | STP |  |
| Custom 35 | STP |  |
| Custom 36 | PHC MAIN | X |
| Custom 37 | PHC |  |
| Custom 38 | PHC |  |
| Custom 39 | PHC |  |
| Custom 40 | PHC |  |
| Custom 41 | CHNW MAIN | X |
| Custom 42 | CHNW MOB | X |
| Custom 43 | CNW |  |
| Custom 44 | CNW |  |
| Custom 45 | CNW |  |
| Custom 46 | CHNE MAIN | X |
| Custom 47 | CHNE MOB | X |
| Custom 48 | CNE |  |
| Custom 49 | CNE |  |
| Custom 50 | CNE |  |
| Custom 51 | AMH MAIN | X |
| Custom 52 | AMH MOB | X |
| Custom 53 | AMH |  |
| Custom 54 | AMH |  |
| Custom 55 | AMH |  |
| Custom 56 | MBMC MAIN | X |
| Custom 57 | MBMC MOB | X |
| Custom 58 | MB |  |
| Custom 59 | MB |  |
| Custom 60 | MB |  |
| Custom 61 | BJHS MAIN | X |
| Custom 62 | BJHS |  |
| Custom 63 | BJHS |  |
| Custom 64 | BJHS |  |
| Custom 65 | BJHS |  |
| Custom 66 | BJHN MAIN | X |
| Custom 67 | BJHN |  |
| Custom 68 | BJHN |  |
| Custom 69 | BJHN |  |
| Custom 70 | BJHN |  |
| Custom 71 | PWDC | X |
| Custom 72 | PWDC-Read Only | X |
| Custom 73 | PWDC |  |
| Custom 74 | PWDC |  |
| Custom 75 | PWDC |  |
| Custom 76 | CSCC |  |
| Custom 77 | CSCC |  |
| Custom 78 | CSCC |  |
| Custom 79 | CSCC |  |
| Custom 80 | CSCC |  |
| Custom 81 | Available |  |
| Custom 82 | Available |  |
| Custom 83 | Available |  |
| Custom 84 | Available |  |
| Custom 85 | Available |  |
| Custom 86 | SSC |  |
| Custom 87 | SSC |  |
| Custom 88 | SSC |  |
| Custom 89 | SSC |  |
| Custom 90 | SSC |  |
| Custom 91 | MHB Main |  |
| Custom 92 | MHB |  |
| Custom 93 | MHB |  |
| Custom 94 | MHB |  |
| Custom 95 | MHB |  |
| Custom 96 | MHE Main |  |
| Custom 97 | MHE |  |
| Custom 98 | MHE |  |
| Custom 99 | MHE |  |
| Custom 100 | MHE |  |

Note: Categories 101-150 Are still available have not yet been assigned to a site

# Appendix B: BJC- BACnet Network Tracking Worksheet v.1.1

See the BJC BACnet Tracking List

# Appendix C: Database Generation Checklist

| Item | Information |
| --- | --- |
| Addressing Scheme | - Static IPs for network devices - Instance ID’s for engines and trunks |
| Naming Conventions - Engines - Field Buses - Controllers - Objects | - All objects require a “system.object” naming convention |
| Alarm Routing - What - Where - When | - Routing based on alarm priority, category, status and time of day and destination. - Paging need to be setup as defined by HSO? - All Alarms 90 second delay minimum |
| Alarm Conventions - Alarm text message standards - Alarm priority determination | - Zone alarms - AHU alarm limits - HW and CHW system alarm limits - Alarm setup for Graphics+ room temperature maps - Command / Status alarms with delay on all fans, pumps and motors |
| Alarm Shutdown | - Define for all systems that can use the Autoshutdown feature when false alarms are not desired - Have startup delay times based on system type |
| Trending Requirements | - Critical Zone objects - AHU objects - HW and CHW objects - Other objects as defined by HSO |
| Trend Study Requirements | - As Defined by HSOs |
| Object Totalization | - Runtime for Fans and Pumps - Consumption for meters - Event for large equipment (Chillers) |
| Scheduling and Calendars | - Organization of schedules and system objects |
| Optimum Start Stop | - As Defined by HSOs |
| Programming - LCT, Interlocks - MC, Signal Select - Global Data Sharing | - Naming standards (“system.object”) - Folder standards (by system) |
| User Views | - Match facility layout - Consider operator use of use - Utilize Tailored Summaries where possible for table views |
| Tailored Summaries - Terminal Equipment - AHU systems - Diagnostic | - Used for terminal equipment - Inputs and Outputs needed for commissioning - Add graphic object link to controller objects |
| Graphics Plus | - All systems, floors, home page and summaries - Navigation scheme – site/building/floor/zone - Add graphic object link to controller objects |
| Object Lists | - Any scheduled reports needed for Joint Commission |
| Other | - MetasysSysAgent account must have password changed from default |

# Appendix F: Process Flow Maps