Copyright 2013 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 078413 - PENETRATION FIRESTOPPING

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

SUMMARY

Section Includes:

Penetrations in fire-resistance-rated walls.

Penetrations in horizontal assemblies.

Penetrations in smoke barriers.

PREINSTALLATION MEETINGS

Preinstallation Conference: Conduct conference at [Project site] <Insert location>.

ACTION SUBMITTALS

Product Data: For each type of product.

LEED Submittals:

"Product Data for Credit IEQ 4.1" Subparagraph below applies to LEED-NC, LEED-CI, and LEED-CS; coordinate with requirements selected in Part 2.

Product Data for Credit IEQ 4.1: For penetration firestopping sealants and sealant primers, documentation including printed statement of VOC content.

"Laboratory Test Reports for Credit IEQ 4.1" Subparagraph below applies to LEED for Schools.

Laboratory Test Reports for Credit IEQ 4.1: For penetration firestopping sealants and sealant primers, documentation indicating that products comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Product Schedule: For each penetration firestopping system. Include location, illustration of firestopping system, and design designation of qualified testing and inspecting agency.

Retain "Engineering Judgments" Subparagraph below only after verifying that authorities having jurisdiction will accept modifications handled by method in subparagraph.

Engineering Judgments: Where Project conditions require modification to a qualified testing and inspecting agency's illustration for a particular penetration firestopping system, submit illustration, with modifications marked, approved by penetration firestopping system manufacturer's fire-protection engineer as an engineering judgment or equivalent fire-resistance-rated assembly. Obtain approval of authorities having jurisdiction prior to submittal.

INFORMATIONAL SUBMITTALS

Product test reports.

CLOSEOUT SUBMITTALS

Installer Certificates: From Installer indicating that penetration firestopping systems have been installed in compliance with requirements and manufacturer's written instructions.

QUALITY ASSURANCE

Retain "Installer Qualifications" Paragraph below, or delete this article if allowing each trade to firestop penetrations they create is acceptable. If retaining, verify that installers are available to perform work in Project location. A list of FM Global-approved firestop contractors may be found in FM Global's "Building Materials Approval Guide," and a list of UL-qualified firestop contractors may be found on www.ul.com/contractor. A list of firestop contractors who are approved or qualified and are also members of Firestop Contractors International Association may be found at www.fcia.org.

Installer Qualifications: A firm that has been approved by FM Global according to FM Global 4991, "Approval of Firestop Contractors," or been evaluated by UL and found to comply with its "Qualified Firestop Contractor Program Requirements."

PRODUCTS

Manufacturers and products listed in SpecAgent and Masterworks Paragraph Builder are neither recommended nor endorsed by the AIA or ARCOM. Before inserting names, verify that manufacturers and products listed there comply with requirements retained or revised in descriptions and are both available and suitable for the intended applications. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

PERFORMANCE REQUIREMENTS

Fire-Test-Response Characteristics:

Perform penetration firestopping system tests by a qualified testing agency acceptable to authorities having jurisdiction.

Test per testing standards referenced in "Penetration Firestopping Systems" Article. Provide rated systems complying with the following requirements:

Penetration firestopping systems shall bear classification marking of a qualified testing agency.

Retain only those subparagraphs below that reference the directories of testing and inspecting agency or agencies approved by authorities having jurisdiction.

UL in its "Fire Resistance Directory."

Intertek Group in its "Directory of Listed Building Products."

FM Global in its "Building Materials Approval Guide."

<Insert name of qualified testing and inspecting agency>.

PENETRATION FIRESTOPPING SYSTEMS

Penetration Firestopping Systems: Systems that resist spread of fire, passage of smoke and other gases, and maintain original fire-resistance rating of construction penetrated. Penetration firestopping systems shall be compatible with one another, with the substrates forming openings, and with penetrating items if any.

<Double click here to find, evaluate, and insert list of manufacturers and products.>

Penetrations in Fire-Resistance-Rated Walls: Penetration firestopping systems with ratings determined per ASTM E 814 or UL 1479, based on testing at a positive pressure differential of 0.01-inch wg (2.49 Pa).

Rating in "F-Rating" Subparagraph below indicates resistance to flame spread.

F-Rating: Not less than the fire-resistance rating of constructions penetrated.

Penetrations in Horizontal Assemblies: Penetration firestopping systems with ratings determined per ASTM E 814 or UL 1479, based on testing at a positive pressure differential of 0.01-inch wg (2.49 Pa).

Ratings in "F-Rating" Subparagraph below indicate resistance to flame spread.

F-Rating: At least one hour, but not less than the fire-resistance rating of constructions penetrated.

Ratings in "T-Rating" Subparagraph below indicate resistance to excessive thermal transmission.

T-Rating: At least one hour, but not less than the fire-resistance rating of constructions penetrated except for floor penetrations within the cavity of a wall.

Ratings in "W-Rating" Subparagraph below indicate resistance to water leakage. W-ratings are not required by the IBC but may be needed if water leakage is a concern.

W-Rating: Provide penetration firestopping systems showing no evidence of water leakage when tested according to UL 1479.

Retain "Penetrations in Smoke Barriers" Paragraph below if smoke barriers are included in Project, and indicate locations on Drawings.

Penetrations in Smoke Barriers: Penetration firestopping systems with ratings determined per UL 1479, based on testing at a positive pressure differential of 0.30-inch wg (74.7 Pa).

Ratings in "L-Rating" Subparagraph below indicate resistance to air leakage.

L-Rating: Not exceeding 5.0 cfm/sq. ft. (0.025 cu. m/s per sq. m) of penetration opening at and no more than 50-cfm (0.024-cu. m/s) cumulative total for any 100 sq. ft. (9.3 sq. m) at both ambient and elevated temperatures.

Exposed Penetration Firestopping Systems: Flame-spread and smoke-developed indexes of less than 25 and 450, respectively, per ASTM E 84.

Retain "VOC Content" Paragraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.1. Coordinate with product selections in other Part 2 articles to ensure that products comply.

VOC Content: Penetration firestopping sealants and sealant primers shall comply with the following limits for VOC content:

Sealants: 250 g/L.

Sealant Primers for Nonporous Substrates: 250 g/L.

Sealant Primers for Porous Substrates: 775 g/L.

Retain "Low-Emitting Materials" Paragraph below if required for LEED for Schools Credit IEQ 4.1.

Low-Emitting Materials: Penetration firestopping sealants and sealant primers shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Accessories: Provide components for each penetration firestopping system that are needed to install fill materials and to maintain ratings required. Use only those components specified by penetration firestopping system manufacturer and approved by qualified testing and inspecting agency for conditions indicated.

EXECUTION

INSTALLATION

Examine substrates and conditions, with Installer present, for compliance with requirements for opening configurations, penetrating items, substrates, and other conditions affecting performance of the Work.

General: Install penetration firestopping systems to comply with manufacturer's written installation instructions and published drawings for products and applications.

Install forming materials and other accessories of types required to support fill materials during their application and in the position needed to produce cross-sectional shapes and depths required to achieve fire ratings.

After installing fill materials and allowing them to fully cure, remove combustible forming materials and other accessories not forming permanent components of firestopping.

Install fill materials by proven techniques to produce the following results:

Fill voids and cavities formed by openings, forming materials, accessories and penetrating items to achieve required fire-resistance ratings.

Apply materials so they contact and adhere to substrates formed by openings and penetrating items.

For fill materials that will remain exposed after completing the Work, finish to produce smooth, uniform surfaces that are flush with adjoining finishes.

IDENTIFICATION

Wall Identification: Permanently label walls containing penetration firestopping systems with the words "FIRE AND/OR SMOKE BARRIER - PROTECT ALL OPENINGS," using lettering not less than 3 inches (76 mm) high and with minimum 0.375-inch (9.5-mm) strokes.

Locate in accessible concealed floor, floor-ceiling, or attic space at 15 feet (4.57 m) from end of wall and at intervals not exceeding 30 feet (9.14 m).

Retain "Penetration Identification" Paragraph below if required. Individual joint penetration labeling may not be required by authorities having jurisdiction if wall is identified, but labeling is useful if penetration firestopping systems must be replaced.

Penetration Identification: Identify each penetration firestopping system with legible metal or plastic labels. Attach labels permanently to surfaces adjacent to and within 6 inches (150 mm) of penetration firestopping system edge so labels are visible to anyone seeking to remove penetrating items or firestopping systems. Use mechanical fasteners or self-adhering-type labels with adhesives capable of permanently bonding labels to surfaces on which labels are placed. Include the following information on labels:

The words "Warning - Penetration Firestopping - Do Not Disturb. Notify Building Management of Any Damage."

Contractor's name, address, and phone number.

Designation of applicable testing and inspecting agency.

Date of installation.

Manufacturer's name.

Installer's name.

FIELD QUALITY CONTROL

If required, inspection of penetration firestopping systems in this article is performed according to ASTM E 2174, "On-Site Inspection of Installed Fire Stops." To prevent conflicts of interest, ASTM E 2174 precludes making Contractor responsible for engaging the testing agency. Inspectors may verify compliance by destructive examination of some completed installations.

Owner will engage a qualified testing agency to perform tests and inspections according to ASTM E 2174.

Where deficiencies are found or penetration firestopping system is damaged or removed because of testing, repair or replace penetration firestopping system to comply with requirements.

Proceed with enclosing penetration firestopping systems with other construction only after inspection reports are issued and installations comply with requirements.

END OF SECTION 078413