SECTION 22 62 22 – Laboratory Vacuum pump Systems (liquid seal)

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

Specifications throughout all Divisions of the Project Manual are directly applicable to this Section, and this Section is directly applicable to them.

SUMMARY

This section includes the furnishing of all labor and materials necessary for complete installation, cleaning, testing, start-up and certification of laboratory vacuum pump system, including; pumps, receiver tank, controls, interconnecting piping, local alarms, remote alarm contacts, valves, supports, and all related accessories.

REFERENCE STANDARDS

The latest published edition of a reference shall be applicable to this Project unless identified by a specific edition date.

All reference amendments adopted prior to the effective date of this Contract shall be applicable to this Project.

All materials, installation and workmanship shall comply with the applicable requirements and standards addressed within the following references:

NFPA 99	Standard for Health Care Facilities.

NFPA 70	National Electrical Code.

qualifications

General: Companies specializing in manufacturing, installing, testing, certifying and servicing the products and systems specified in this section shall have minimum five years documented experience and be certified as required by the authorities having jurisdiction and NFPA 99.

Manufacturers: Firms regularly engaged in manufacture of medical vacuum systems equipment and products, of types, materials, and sizes required, whose products have been in satisfactory use in similar service for not less than 5 years. References may be required.

Equipment Supplier: The medical vacuum systems equipment supplier shall provide the services of a manufacturer authorized product specialist to periodically coordinate with the installing Contractor during initial installation of the pipeline systems and have a service organization located within 50 miles of the project Site to provide ongoing service support to BJC HEALTHCARE after project completion.

Installer: Firm with at least 5 years of successful installation experience on projects with medical gas systems work similar to that required for project. All installations of the medical vacuum piping systems shall be done only by, or under the direct supervision of a holder of a mechanical pipefitter license or a journeyman pipefitter license with a medical gas piping installation endorsement issued by the authorities having jurisdiction. All installers of medical gas system components must be qualified in accordance with the requirements of NFPA 99 and ASSE 6010, Medical Gas Systems Installers Professional Qualifications Standard. In addition, all brazers of medical gas system piping must be qualified in accordance with the requirements of either Section IX, Welding and Brazing Requirements of the ASME Boiler and Pressure Vessel Code, or AWS B2.2, Standard for Brazing Procedure and Performance Qualification.

System Verification Testing Agency: Testing shall be conducted by a party technically competent and experienced in the field of medical gas and vacuum pipeline testing and meeting the requirements of ANSI/ASSE Standard 6030, Medical Gas Verifiers Professional Qualifications Standard. Quality control standards of testing agency shall be in strict accordance with American National Standards Institute (ANSI) Q-91. Firm shall be regularly engaged in the testing and certification of similar facilities with a minimum of 5 years of experience.

QUALITY ASSURANCE

All materials, equipment, installation, testing and certification shall be in strict accordance with NFPA 99 for Level 1 Medical–Surgical Vacuum and WAGD.

Manufacturer’s name, address and contact information shall be permanently labeled on equipment.

Maintain one copy of each Contract Document on Site.

Prior to any installation Work, the installer of medical vacuum piping shall provide and maintain documentation on the job Site for the qualification of brazing procedures and individual brazers as required by NFPA 99.

SUBMITTALS

General:

All submitted data shall be specific to this project and identified as such. Generic submittal data will not be accepted.

Product Data:

Manufacturers descriptive literature, illustrations and installation instructions for all components included within this project indicating compliance with applicable referenced standards, size, dimensions, model number, electrical characteristics, support and connection requirements.

Shop Drawings:

Wiring diagrams for laboratory vacuum source equipment system. Differentiate between manufacturer-installed and field-installed wiring.

Record Documents:

Record actual locations of equipment, piping, valves and controls.

Provide record of test procedures and the results of all tests indicating room and area designations, dates of the tests, and names of persons conducting the tests.

Brazer Certificates: Installation Contractor shall present written documentation (less than 1 year old) from a recognized agency trained in administering and testing brazing techniques as per AWS B2.2 or ASME Section IX, certifying that all brazers have been thoroughly trained and tested in the complete installation of medical gas systems.

Inspection and Test Reports: Furnish documentation that all installer inspections and tests required by NFPA 99 for Level 1 Medical–Surgical Vacuum and WAGD have been performed. Identify test type, procedure and results.

Independent Third Party System Verification Testing Agency Reports and Certification: Documentation verifying that completed systems have been installed, tested, purged, and analyzed in accordance with the requirements of referenced standards and Contract Documents. Provide copy of agency’s written Q-91 standards.

Statement of Warranty: Provide equipment manufacturers Statement of Warranty for all furnished equipment and components. Warranty shall specifically indicate project by name and date of equipment start-up.

Provide full written description of manufacturer’s warranty.

Operation and Maintenance Data:

Operation Data: Include manufacturer’s installation and operating instructions.

Maintenance Data: Servicing requirements, inspection data, preventative maintenance schedule, exploded assembly views, replacement part numbers and availability, location and contact numbers of service depot.

DELIVERY, STORAGE and HANDLING

Equipment and components shall arrive on-Site properly protected and undamaged with containers, packaging and labels intact.

Each pipe and tank opening shall be delivered plugged or capped by the manufacturer and kept sealed until prepared for installation.

Loose fittings, valves, gauges and other components shall be delivered sealed, labeled, and kept sealed until installation.

Store, handle and protect materials and equipment in accordance with Manufacturer's recommendations.

Provide equipment and personnel necessary to handle equipment and components by methods to prevent damage to  products or packaging. Provide additional protection during handling as necessary to prevent breaking scraping, marring, or otherwise damaging products or surrounding areas.

Lift heavy components only at designated lifting points.

Protect all equipment and components that are to be installed within this project from theft, vandalism, and exposure to rain, freezing temperatures and direct sunlight.

Protect installed equipment and components from damage and prevent use.

scheduling

Schedule Work to ensure installation is complete, tested and certified prior to Substantial Completion.

warranty

Manufacturer shall warrant furnished equipment and components to be free of defects in material and workmanship under normal use for a period of thirty-six (36) months from date of start-up.

PRODUCTS

GENERAL

All materials shall meet or exceed all applicable referenced standards, federal, state and local requirements, and conform to codes and ordinances of authorities having jurisdiction.

The laboratory vacuum system shall be factory assembled as a complete package and be fully compliant with the latest edition of NFPA 99.  The package shall be a muti-plex closed loop, air cooled, oil-sealed liquid ring vacuum pump system including pumps, motors, a control panel, fuel separator reservoirs, air-cooled heat exchangers, receiver tank, interconnecting piping, interconnecting wiring and optional accessories indicated herein, all mounted on a common base frame designed to provide sufficient support to all major system components, including interconnecting piping. Each pump and the receiver shall be connected to common piping manifold arranged to provided a single connection to the receiver intake and a single point of connection to the exhaust of the system.  A single point of connection to the electrical panel of the system shall be provided.  The complete vacuum pump system shall be tested by the manufacturer before shipment to ensure that all system components and electrical control instruments function properly. This includes a complete cycle test, which simulates actual operating conditions.

The system must be capable of operating in moist or wet inlet conditions and have the ability to pass soft solids or liquids without serious damage to the pump. The system shall have a maximum operating noise level of 80 dBA at 3 feet distance.  No enclosure shall be required to dampen sound or hamper maintenance or access to the equipment.  Vacuum pumps shall have a maximum rotor speed of 1800 rpm.  The vacuum system must be able to operate continuously at ambient temperatures up to 110º F without overheating.

The Contractor shall ascertain for himself the space and access available for the installation of a factory assembled packaged unit and, as an option, may furnish factory assembled modular units and interconnect the various components in place at the Site in lieu of providing a factory assembled packaged unit.  However, all components shall be compatible and be tested as a complete system prior to shipment, and be furnished by a single source manufacturer. All electrical services and interconnecting equipment wiring and piping must be provided for within this Contractor’s bid.

Each vacuum pump shall have a factory piped intake to the receiver with NFPA 99 compliant integral flex connector, isolation valve, and check valve.

An automatic means shall be provided to prevent backflow from any on-cycle vacuum pumps through any off-cycle vacuum pumps.

A shutoff valve and check valve shall isolate each vacuum pump from the centrally piped system and other vacuum pumps for maintenance or repair without loss of vacuum in the system.

Piping shall be arranged to permit service and a continuous supply of medical–surgical vacuum in the event of a single fault failure.

Refer to Laboratory Vacuum Pump schedule on Contract Drawings for required quantity of pumps, capacities, receiver size and electrical characteristics.

Laboratory vacuum pump system System design must be equal in all aspects to the “Vmax” system manufactured by Dekker Vacuum Technologies, Inc.

Vacuum Pumps

The vacuum pumps shall be of the single-stage liquid ring type manufactured to ISO9001 quality standards, with cast iron casing, ductile iron, bronze or stainless steel impeller and stainless steel shaft. Shaft seals shall be carbon face mechanical seals, with Viton elastomers. Packed glands or stuffing box designs are not acceptable.  Only pumps with flat port plate design are to be considered. Pumps, which require internal lubrication for bearings, vanes or rotors, are not acceptable.

Each vacuum pump shall have a minimum inlet SCFM capacity as scheduled on Contract Drawings at an inlet vacuum of 29 inches Hg.

Each pump must be able to operate below 15” Hg for an extended period of time without any operational problems and capable of operating up to a maximum vacuum of 29” Hg (at sea level).

To avoid misalignment in the field, the pumps must be, whenever possible, of the direct driven monoblock flange mounted design to fit a standard NEMA design C-flange motor. V-belt  driven units up to 40 Hp are not acceptable.

fluid separator reservoir

The oil separator reservoir shall be a cylindrical design of sufficient capacity and shall include a five (5) stage separator arrangement, which includes a thermodynamic stage and several mechanical baffles for proper air/oil separation. The final stage should include an internally mounted two (2) stage high efficiency coalescing separator element, adequately sized to allow a maximum initial pressure drop of 1 psig at an operating vacuum of 15” Hg and insure a 99.99% oil recovery rate. The reservoir shall have a removable top cover for easy access to the internal filter and include a pressure indicator to show the condition of the separator element. An oil level and temperature gauge showing reservoir oil level and system operating temperature shall be included. An oil scavenger line with orifice must be provided and properly connected. The separator/reservoir must be overhead mounted to ensure positive oil flow without the use of a circulation pump and must be equal to DVT’s “DX-5” system. The oil return line to the vacuum pump shall include a filter/strainer to separate any solids or impurities carried over into the system. Spin-on oil filters are not acceptable. The filter/strainer with cleanable replaceable screen must be fitted with an isolation valve. A solenoid valve of zero pressure differential shall be provided to control oil flow from the oil reservoir.

seal fluid cooler

The cooling of the sealing fluid shall be done through an integral air-cooled heat exchanger design with high flow cooling fan driven from the main vacuum pump motor. Heat exchangers with separate electric motor driven cooling fans are not acceptable.

seal fluid

The system shall be supplied with one full charge of DVT Vmaxol long life seal fluid designed specifically for liquid ring vacuum pumps with a service life of minimum 10,000 hours under normal operating conditions.

safety devices

The vacuum pump shall include a high temperature shutdown switch to protect the pump against high temperature operation or in case of an interruption of the seal fluid supply.

A low oil level switch shall be fitted in the oil reservoir, which will shut down the system in case of a sudden oil loss.

An audible alarm w/dry NC contact shall be fitted to the control panel, which is activated during the above condition.

suction line components

An Automatic electrical inlet check valve designed for vacuum service with soft seat and minimal restriction shall be installed on the inlet of each vacuum pump.

An Anti-suck-back valve designed to stop fluid from being extracted from another pump, and to prevent the pump from turning backwards when de-energized shall be installed on each pump.

A vacuum gauge with a minimum of 2-1/2” dial, fluid filled shall be provided.

laboratory vacuum receiver

A receiver tank shall be provided to add capacity to the vacuum piping system in order to reduce frequent cycling of a pump operating on a vacuum switch. Intake piping from each vacuum pump shall be manifolded and connected to the receiver tank at the factory in order for the receiver to function as a dropout tank to help prevent carry-over of solids or liquids into the pumps.

The vacuum receiver shall Comply with Section VIII, Unfired Pressure Vessels, of the ASME Boiler and Pressure Vessel Code, be ASME Code stamped, and rated for a minimum 150 PSIG design pressure.

The vacuum receiver shall be capable of withstanding a gauge pressure of 415 kPa (60 psi) and 760 mm (29.9 in.) gauge HgV.

Tank interior shall be epoxy coated for corrosion resistance.

The receiver shall be provided with a sight/level gauge, a manual drain and have a three valve bypass system to allow for draining of the receiver without interrupting the vacuum service.

Receiver shall have capacity and physical dimensions as scheduled on Contract Drawings.

electric motors

Motors up to 20 HP shall be of a standard NEMA C-Flange design, to allow pump and motor alignment and be suitable for continuous operation. Motor size shall have horsepower and voltage as scheduled on Contract Drawings and be 3 phase, 60 HZ, TEFC enclosure, high efficiency design (minimum 91%).

control system

The control system shall be NEMA 12 and U.L. labeled.

The control system shall provide automatic lead/lag sequencing with circuit breaker disconnects for each vacuum pump having external operators and safety door, full voltage motor starters with overload protection and redundant 120 volt control circuit transformers with fused primary and secondary.

The control system shall include hand-off auto lighted selector switches and runtime hour meters.

The control system shall provide a local visual and audible reserve unit alarm with isolated contacts for remote alarm. Alarm shall indicate back-up or lag vacuum pump in operation when the primary or lead vacuum pump is incapable of satisfying the demand of the requirements of the system, except when the vacuum pump system consists of three or more pumps, then the back-up or lag signal shall energize when the last pump has been signaled to start.

A programmable logic controller shall control the automatic alteration of the vacuum pumps with provisions for simultaneous operation, and automatic activation of reserve unit.

Control circuits shall be arranged in such a manner that the shutdown of one pump does not interrupt the operation of another pump.

The control system shall include an automatic minimum run time adjustment to control run time based on demand.

A vacuum gauge shall be provided in the control panel.

laboratory vacuum pump system piping

Interconnecting piping within the medical vacuum pump system and all exhaust piping shall be Type "K" or “L” hard-drawn seamless copper, either ASTM B 819 medical gas tube or ASTM B 88 water tube.

Turns, offsets, and other changes in direction shall be made with brazed wrought copper capillary fittings complying with ANSI B16.22, Wrought Copper and Copper Alloy Solder-Joint Fittings; or brazed fittings complying with MSS SP-73, Brazed Joints for Wrought and Cast Copper Alloy Solder Joint Pressure Fittings. Cast copper alloy fittings shall not be permitted.

Brazed joints shall be made using a brazing alloy that exhibits a melting temperature in excess of 538°C (1000°F). Copper-to-copper joints shall be brazed using a copper–phosphorus or copper–phosphorus–silver brazing filler metal (BCuP series) without flux. Flux shall only be used when brazing dissimilar metals such as copper and bronze or brass, using a silver (BAg series) brazing filler metal. Brazing alloy comply with ANSI/AWS A.5.8, Specification for Brazing Filler Metal.

Threaded joints in medical vacuum piping shall be limited to connections to pressure/vacuum indicators, alarm devices, and connections to equipment. All threads shall be tapered pipe threads complying with ANSI B1.20.1, Pipe Threads, General Purpose and be made up with polytetrafluoroethylene (such as Teflon™) tape or other thread sealant recommended for oxygen service, with the sealant applied to the male threads only. Where threaded nipples are required, these shall be I.P.S. brass.

Mechanically formed, drilled and extruded tee-branch connections are not permitted.

Couplings and fittings incorporating an o-ring seal are not permitted.

Roll-grooved joints are not permitted.

Straight-threaded connections, including unions, flared and compression-type connections, are not permitted.

Seal fluid supply lines shall be Aeroquip MatchMate Plus or equal high-pressure hose with crimp on fittings. Rigid steel pipe with screwed fittings is not acceptable because of potential seal fluid leaks from pipe joints.

laboratory vacuum shut-off valves

Shut-off valves shall be full port, double seal, ball-type three piece design, designed for vacuum to 29 inches Hg and working pressures up to 600 WOG with bronze/brass body, blow-out proof stem and chrome plated brass ball and be serviceable in the line. Valve body shall have Teflon™ (TFE) material ball seat and stem seals. Seats/seals, lubricants and valve material shall be compatible with medical oxygen, nitrous oxide, compressed air, carbon dioxide, nitrogen and mixtures thereof at continuous pressure up to 600 psig and up to 100 degrees Fahrenheit.

Valve shall be provided with and operated by a lever-type handle requiring only a quarter turn from a fully open position to a fully closed position.

laboratory vacuum check valves

Check valves shall be center guided, self-aligning, spring loaded ball type check with brass body, Teflon seat, straight-through flow, 400 psi WOG minimum working pressure, having vibration free, silent operation.

Check valves shall be 100% leak tested and comply with NFPA 99.

EXECUTION

INSTALLATION

Installation shall meet or exceed all applicable federal, state and local requirements, referenced standards and conform to codes and ordinances of authorities having jurisdiction.

All installation shall be in accordance with manufacturer’s published recommendations.

Install all system components in complete compliance with referenced standards and manufacturer’s published instructions.

Locate equipment with adequate access space for service.  Provide no less than minimum as recommended by manufacturer.

Provide minimum 4” thick reinforced concrete pad with chamfered corners beneath floor mounted equipment. Pads shall extend minimum of 4” on all sides beyond the limits of the mounted equipment unless otherwise noted.

Anti-vibration mountings shall be installed for vacuum pumps as required by equipment dynamics or location and in accordance with the manufacturer’s recommendations.

Flexible connectors shall be used to connect the vacuum pumps with their intake and outlet piping.

Vacuum piping from building distribution system shall connect to receiver tank inlet prior to flowing into pumps.

Locate laboratory vacuum pumps exhaust in a manner and location that will minimize the hazards of noise and contamination to the facility and its environment. The exhaust shall terminate outdoors, at least 25 feet from any door, window, air intake, or other openings in the building; at least 3 feet above all air intakes and where prevailing winds, adjacent buildings, or other influences cannot divert the exhaust into occupied areas or disperse the exhaust.

The exhaust terminal shall be turned down and screened with non-corroding material to protect against the entry of vermin, debris, or precipitation.

The exhaust piping shall be free of dips and loops that might trap condensate or oil. Where such low points are unavoidable, a drip leg and valved drain shall be installed. Vacuum exhausts from multiple pumps shall be joined together to one common exhaust. The common exhaust shall be sized to minimize back-pressure in accordance with the pump manufacturer’s recommendations.

Each pump shall be isolated by a ball valve and a check valve to prevent flow of exhaust air into the room when pumps are removed for service.

Vacuum indicators shall be readable from a standing position.

Provide low voltage wiring from vacuum source equipment to master alarm annunciators as required by NFPA 99. All low voltage wiring shall be routed within conduit.

Coordinate with Electrical Contractor to insure that emergency electrical service is provided for the medical air source equipment conforming to the requirements of the essential electrical system as described in NFPA 99.

Remove all dirt, dust, construction debris and all other foreign materials from installed equipment and components. Equipment finishes shall be free from all rust, scratches, dents, etc. Contractor shall be responsible for all cleaning and re-finishing required to provide Owner with equipment that is in factory-new condition at Substantial Completion of the project. All labels shall be clean and legible.

TESTING and inspection

Inspection and testing shall be performed on medical–surgical vacuum source system before being put into service to assure the facility, by a documented procedure, that all applicable provisions of NFPA 99 have been adhered to, that the system is functioning properly, and system integrity has been achieved or maintained.

System verification tests shall be performed only after all installer performed tests, have been completed. Equipment Vendor or installing Contractor shall not perform system verification, final testing or certification.

It shall be the responsibility of the Third Party Medical Gas System Verification Testing Agency to make periodic job Site visits to assure all requirements of this specification and NFPA 99 are strictly adhered to.

Certification shall clearly state that the system is approved for laboratory use and meets all requirements of NFPA-99 inclusive of all referenced and/or related documents.  Any exceptions or limitations shall be clearly stated on the same certification document.

Vendor supervision

An authorized representative of the equipment manufacturer shall periodically check with the installing Contractor during initial installation of the medical vacuum pump system and shall assist the Contractor in final checking to make certain that all components are operating as recommended by the manufacturer, as specified, and in accordance with NFPA 99. The equipment manufacturer's representative shall provide a minimum of 4 hours instruction to BJC HEALTHCARE personnel in the use, operation and maintenance of the system.

END OF SECTION 22 62 22