SECTION 23 82 19 – fan coil units

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

Specifications throughout all Divisions of the Project Manual are directly applicable to this Section, and this Section is directly applicable to them.

SUMMARY

Fan coil units.

REFERENCE STANDARDS

The latest published edition of a reference shall be applicable to this Project unless identified by a specific edition date.

All reference amendments adopted prior to the effective date of this Contract shall be applicable to this Project.

All materials, installation and workmanship shall comply with the applicable requirements and standards addressed within the following references:

NFPA 70 – National Electrical Code.

ASHRAE Standard 90.1 – “Energy Standard for Buildings Except Low-Rise Residential Buildings”.

ARI 440 – “Room Fan-Coils”.

ANSI/UL-883 – “Safety Standards for Fan Coil Units and Room Fan Heater Units”.

NFPA 90A – “Standard for the Installation of Air Conditioning and Ventilation Systems”.

QUALITY ASSURANCE

Manufacturer:  Company specializing in manufacturing the products specified in this Section with minimum three (3) years documented experience.

SUBMITTALS

Product Data:

Submit product data indicating typical catalog of information including dimensions, weights, capacities, ratings, fan performance, gages and finishes of materials, electrical characteristics and connection requirements.

Submit fan curves with specified operating point clearly plotted.  Fan curves shall clearly demonstrate that the fan coil unit will operate stably within the range of performance scheduled.

Submit coil performance data as tested and certified per ARI standards.

Submit electrical requirements for power supply wiring, clearly indicating factory-installed and field-installed wiring.

The submittal shall indicate that all materials meet NFPA 90 flame/smoke spread levels of 25/50 or better.

Record Documents:

Shop Drawings:  Indicate materials and methods of assembly, unit dimensions, weight loading, required clearances, field connection details, electrical characteristics and dimensional views as required to adequately describe the unit.

Submit manufacturer’s installation instructions.

Submit Record Drawings in accordance with Division 01.

DELIVERY, STORAGE and HANDLING

Deliver, store, and protect products to the Project Site under provisions of Division 01 and Division 20.

Protect units from physical damage by storing in protected areas and leaving factory covers in place.

WARRANTY

Provide one (1) year manufacturer’s warranty.

Include coverage of fan-coil unit and motors.

PRODUCTS

GENERAL

All materials shall meet or exceed all applicable referenced standards, federal, state and local requirements, and conform to codes and ordinances of authorities having jurisdiction.

Units shall bear an ARI stamp.

Fan coil units shall be of the size and configuration as described on the Drawings.

Performance as scheduled on the Drawings shall be a minimum requirement.  Base coil unit performance on sea level conditions.

Fan coil unit height shall be less than or equal to the unit scheduled.

Fan coil unit sizes shall be such that the units can be transported to the area of work and installed within the physical space available.

This Section does not apply to units that condition raw unconditioned outside air.  Refer to Section 23 73 23.

[Note:  Sound data must be added]

manufacturers

Envirotec.

Carrier.

Temtrol

Trane.

York.

CASING AND FRAME

18 gage enclosure, galvanized steel.  Frame shall be galvanized steel members.

Units exposed below deck shall have a baked enamel finish.

Internally insulate units throughout the entire enclosure with 1-inch thick insulation.  Insulation shall have a foil facing on the interior.

Units shall be completely enclosed with all components including the motor, interior to the casing.

Primary Drain Pan:

Units shall have a rust-inhibiting IAQ style drain pan across the full width of the unit, extending from the cooling coil to the end of the unit.

Insulate drain pan.

Drain connection shall be minimum 7/8-inch outside diameter, copper construction.

Arrange coil and drain pan connections on the side of the unit as shown on the Drawings.

Units shall be provided with integral mounting brackets adequate to support the unit’s weight.

Units shall be provided with a discharge and inlet duct collar.

Furnish access doors as required to service all elements of the unit from the sides.  It shall not be necessary to access the bottom of the unit to service any component.

FANS AND RELATED COMPONENTS

Provide single or dual fans with integral direct drive multiple-speed motor or demountable belt drive motor.  Direct drive motor speed shall be set via easily accessible wall-mounted switches.

Motors shall be high efficiency type with built-in thermal overload protection.

All units scheduled for capacities of 1200 cfm or greater shall be externally isolated with spring isolators.

COILS

Cooling Coils:

Copper tube with aluminum fins.

Tubes shall be ½-inch outside diameter with a minimum wall thickness of 0.02 inches.

For units scheduled with capacities of 600 cfm or less, fins shall be spaced no closer than 14 fins per inch and shall have a minimum fin thickness of 0.0075 inches.

Larger capacity units shall have fins spaced no closer than 9 fins per inch and shall have a minimum fin thickness of 0.0088 inches.

Where required, heating coils shall be copper tube with aluminum fins.  Tubes shall be ½-inch outside diameter with a minimum wall thickness of 0.020 inches.  Fins shall be spaced no closer than 14 fins per inch with a minimum fin thickness of 0.0075 inches.

Air velocities across cooling coils shall not exceed 500 fpm.  Air velocities across heating coils shall not exceed 700 fpm.

Coil headers shall be the full size of the coil connection with manual air vents located at the top.

Coil frames shall be heavy duty galvanized steel construction.

FILTERS AND RELATED COMPONENTS

All fan coil units shall have provisions for mounting a filter at the unit inlet.  Filter shall be a standard ½-inch throwaway filter, 30 percent efficiency.

UNIT SPECIALTIES

For each unit, provide a 22 gage sheet metal auxiliary drain pan mounted below the entire unit and primary drain pan.

Auxiliary drain pans shall either be drained to an approved condensate receiving location or shall be provided with a float switch that shall de-energize the fan coil unit and send an alarm to the building automation system (BAS).

ELECTRICAL PROVISIONS

Each unit shall have a single point of power connection pre-wired at the factory.

Starters shall be provided by Division 26.

EXECUTION

PREPARATION

Verify that areas are ready to receive Work and opening dimensions are as indicated on Shop Drawings.

Verify that required utilities are available, in proper location, and ready for use.

INSTALLATION

Installation shall meet or exceed all applicable federal, state and local requirements, referenced standards and conform to codes and ordinances of authorities having jurisdiction.

All installation shall be in accordance with manufacturer’s published recommendations.

Hang units from building structure with pipe hangers anchored to the building, not from piping. Mount units as high as possible to maintain greatest headroom unless otherwise indicated.  Refer to Section 20 05 48 for vibration isolation.

Protect units with protective covers during balance of construction.

Refer to details on the Drawings for piping appurtenances and configuration.

Leave adequate room to access and service all components.

Arrange fan coil units and ductwork such that poor fan performance does not result.

Do not operate units without specified filters being installed.

Mount disconnect switches and starters within sight of the fan motor and independent of the unit to allow for maintenance access.

CLEANING

After construction and painting is completed, clean exposed surfaces of units.  Vacuum clean coils and inside of cabinets.

Touch up marred or scratched surfaces of factory-finished cabinets, using finish materials furnished by manufacturer.

Install new filters after Substantial Completion.

END OF SECTION 23 82 19