SECTION 23 82 39 – Unit Heaters

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

Specifications throughout all Divisions of the Project Manual are directly applicable to this Section, and this Section is directly applicable to them.

SUMMARY

Perform all Work required to provide and install unit heaters indicated by the Contract Documents with supplementary items necessary for proper installation.

REFERENCE STANDARDS

The latest published edition of a reference shall be applicable to this Project unless identified by a specific edition date.

All reference amendments adopted prior to the effective date of this Contract shall be applicable to this Project.

All materials, installation and workmanship shall comply with the applicable requirements and standards addressed within the following references:

NFPA 70 – National Electrical Code.

ASHRAE 90.1 – “Energy Standard for Buildings Except Low-Rise Residential Buildings”.

ARI 440-98 – “Room Fan-Coils”.

ANSI/UL-883 – “Safety Standards for Fan Coil Units and Room Fan Heater Units”.

NFPA 90A – “Standard for the Installation of Air Conditioning and Ventilation Systems”.

QUALITY ASSURANCE

Manufacturer: Company specializing in manufacturing the products specified in this Section with minimum three (3) years documented experience.

SUBMITTALS

Submit under provisions of Division 01 and Division 20.

Product Data:

Submit product data indicating typical catalog of information including dimensions, weights, capacities, ratings, fan performance, gages and finishes of materials, electrical characteristics and connection requirements.

Submit fan curves with specified operating point clearly plotted.  The fan curves shall clearly demonstrate that the fan coil unit will operate stably within the range of performance scheduled.

Submit coil performance data as tested and certified per ARI standards.

Submit electrical requirements for power supply wiring, clearly indicating factory-installed and field-installed wiring.

The submittal shall indicate that all materials meet NFPA 90 flame/smoke spread levels of 25/50 or better.

Submit manufacturer’s installation instructions.

Record Documents:

Shop Drawings:  Indicate materials and methods of assembly, unit dimensions, weight loading, required clearances, field connection details, electrical characteristics and dimensional views as required to adequately describe the unit.

DELIVERY, STORAGE and HANDLING

Deliver products to the Project Site and store and protect products under provisions of Division 01 and Division 20.

Protect units from physical damage by storing in protected areas and leaving factory covers in place.

PRODUCTS

GENERAL

All materials shall meet or exceed all applicable referenced standards, federal, state and local requirements, and conform to codes and ordinances of authorities having jurisdiction.

Coils:

Seamless copper tubing, 0.025 inch minimum wall thickness.

Silver brazed to steel headers with evenly spaced aluminum fins mechanically bonded to tubing rated at system working pressures as indicated on Drawings.

All valves shall be outside of unit for gauge cocks and thermometer wells.

Casing: 18-gage steel with threaded pipe connections for hanger rods.

Finish: Factory applied baked enamel of a color as selected by the Architect on visible surfaces of enclosure or cabinet.

Fan:

Direct drive propeller type, statically and dynamically balanced, with fan guard.

Horizontal models with permanently lubricated sleeve bearings.

Vertical models with grease lubricated ball bearings.

Air Outlet: Adjustable pattern diffuser on projection models and four way louvers on horizontal throw models.

Motor:

Refer to Section 20 05 13.

Horizontal models with permanently lubricated sleeve bearings.

Vertical models with grease lubricated ball bearings.

manufacturers

Modine

Reznor

Trane

EXECUTION

PREPARATION

Verify that surfaces are ready to receive work and opening dimensions are as indicated on Shop Drawings.

Verify that required utilities are available, in proper location and ready for use.

INSTALLATION

Installation shall meet or exceed all applicable federal, state and local requirements, referenced standards and conform to codes and ordinances of authorities having jurisdiction.

All installation shall be in accordance with manufacturer’s published recommendations.

Hang unit heaters from building structure with pipe hangers anchored to the building, not from piping.  Mount units as high as possible to maintain greatest headroom unless otherwise indicated on the Drawings.   Refer to Section 20 05 48 for vibration isolation.

Install unit heaters exposed to finished areas, after walls and ceiling are finished and painted. Avoid damage.

Protect units with protective covers during balance of construction.

Provide hydronic units with shut-off valve on supply and lockshield balancing valve on return piping.  If not easily accessible, extend vent to exterior surface of cabinet for easy servicing. For cabinet unit heaters provide float operated automatic air vents with stop valve.

Leave adequate room to access and service all components.

Cleaning

After construction and painting is completed, clean exposed surfaces of units.  Vacuum clean coils and inside of cabinets.

Touch-up marred or scratched surfaces of factory-finished cabinets, using finish materials furnished by manufacturer.

Install new filters after Substantial Completion.

END OF SECTION 23 82 39