SECTION 23 84 14 – electric steam grid humidifiers

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

Specifications throughout all Divisions of the Project Manual are directly applicable to this Section, and this Section is directly applicable to them.

SUMMARY

Perform all Work required to provide and install electric steam humidifiers with steam jacketed distribution manifolds indicated by the Contract Documents with supplementary items necessary for proper installation.

REFERENCE STANDARDS

The latest published edition of a reference shall be applicable to this Project unless identified by a specific edition date.

All reference amendments adopted prior to the effective date of this Contract shall be applicable to this Project.

All materials, installation and workmanship shall comply with the applicable requirements and standards addressed within the following references:

ARI 610 - Central System Humidifiers.

ARI 630 - Selection, Installation and Servicing of Humidifiers.

QUALITY ASSURANCE

Manufacturer Qualifications: Company specializing in manufacturing the products specified in this Section with three (3) years documented experience.

SUBMITTALS

Product Data:

Submit product data and Shop Drawings indicating type, size, location, application, and capacity.

Operation and Maintenance Data:

Submit manufacturer's installation instructions and operating and maintenance data.

extra materials

Provide six extra disposable humidifier cylinders for each unit.

warranty

Provide a two (2) year warranty including coverage for humidifier unit except the cylinder.

PRODUCTS

GENERAL

All materials shall meet or exceed all applicable referenced standards, federal, state and local requirements, and conform to codes and ordinances of authorities having jurisdiction.

manufacturers

Nortec Model NHMC.

Dri-Steem Humidifiers Co.

DGH System, Inc.

Armstrong Model AMR.

Or accepted substitution.

Steam humidifiers

Furnish and install steam humidifiers of the sizes and capacities shown on the Drawings.

Humidifiers shall be of the multiple dispersion tube, steam injection, dry type wherein entrained condensate is removed from the steam by means of 304 stainless steel, centrifugal type, water/steam separators.

Humidifiers shall be designed and catalogued to accomplish 100 percent absorption within three (3) feet downstream of the humidifier when air is at 95 percent relative humidity.

Electrode Steam Generating Type Humidifier:

CSA certified and UL listed.

Disposable cylinder type.

Electronic capacity control (20 percent to 100 percent).

Proportional and integral auto-adaptive control to automatically adapt to incoming water condition.

Alphanumeric LCD display which can indicate system messages, output, control signal input, capacity demand, and system configuration.

Keypad to configure, monitor and control humidifier with information messages on LCD display.

Self-diagnostic controls on start-up and during operation shall prevent unsafe operation of the unit.

Solenoid control of supply and drain water.

Automatic self-help feature that can clean obstruction from the drain valve when needed.

Automatic off-season shutdown that will completely drain the cylinder during prolonged off periods and restart automatically on a call for humidity.

Full front access.

Constant Volume Control System:  The humidifier shall be controlled by a humidistat, airflow proving switch and high limit control that automatically shuts humidifier down when the humidity level in the duct increases above 80 percent to 85 percent relative humidity. Prevents wetting of the ductwork.

Variable Volume Control System: The humidifier shall be controlled by a humidistat, airflow proving switch and modulating high limit control that will automatically reduce the output capacity of the humidifier when the humidity level in the duct increases above 80 percent to 85 percent relative humidity. Prevents wetting of ductwork when airflow is decreased.

Dual cylinder units shall have dual control circuits for complete control of each cylinder and safety.

Steam distributor with condensate separator.

Remote message indication capability to indicate normal operation, change cylinder and shutdown shall be standard.

Cal-rod heater element electric humidifiers not acceptable.

Accessories

Supply and install the following accessories in accordance with the manufacturer's recommendation.  Accessories based on Nortec Model NHMC.

132-9203:  Duct mounted pressure differential switch for air proving interlock.

146-9321 through 146-9330:  Proportional modulating control. Allows full modulating control of humidifiers by varying signals from control systems supplied by others.  Most variable DC voltage, resistance and current signals can be accommodated.

132-9505:  Inline water filter for supply water.

146-9533:  Fill cup extension kit for NH-005 through NH-030.  Required when duct static and steam line resistance exceeds standard unit limitations.

132-8810:  Steam hose 7/8 inch ID for ASD and BSD type steam distributors used with NH-005 through NH-030 units.

132-8840:  Condensate return hose 3/8-inch ID.  Used with all units.

146-9525 and 146-9529:  Remote service indicator package provides an audible and visual indication remotely from the humidifier when any service code appears.

146-9522:  Low temperature protection.  Activates humidifier independent of humidistat if internal temperature falls below set point.  Two (2) required for NH-150 and NH-200.

High limit stat to deactivate steam control valve when the high limit is 90 percent or higher.

Provide a building automation system (BAS) interface card to receive signals from the BAS for controlling the control valve of each humidifier.

EXECUTION

INSTALLATION

Installation shall meet or exceed all applicable federal, state and local requirements, referenced standards and conform to codes and ordinances of authorities having jurisdiction.

All installation shall be in accordance with manufacturer’s published recommendations.

Install in accordance with ARI 630.

Provide galvanized steel rods to support distribution manifolds and mount in air system plenums.

Connect outlet of unit to drain piping. Provide gate valve.

Install cold water supply of ¼-inch type K soft copper tubing with shutoff cock and 7/8 inch drain line. Pipe drain to nearest floor drain ensuring air gap is incorporated per manufacturer's instructions.

Mount airflow switch and tubing.

Install unit in duct with at least six (6) feet of straight run downstream of humidifier for steam to be absorbed into the air stream. Provide the minimum number of dispersion tubes (manifold) to achieve complete absorption in the short run.

testing

Operate humidifiers only when airflow is proven.

Start-up by a factory trained technician.

END OF SECTION 23 84 14