SECTION 26 28 17 – Motor and circuit disconnectS

GENERAL

RELATED DOCUMENTS

Shop Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

Specifications throughout all Divisions of the Project Manual are directly applicable to this Section, and this Section is directly applicable to them.

SUMMARY

This Section specifies the requirements for disconnect switches, fusible and nonfusible.

REFERENCE STANDARDS

The latest published edition of a reference shall be applicable to this Project unless identified by a specific edition date.

All reference amendments adopted prior to the effective date of this Contract shall be applicable to this Project.

All materials, installation and workmanship shall comply with the applicable requirements and standards addressed within the following references:

Federal Spec. W-S-865 - Switch, Box (Enclosed), Surface Mounted.

NEMA KS 1 - Enclosed Switches.

SUBMITTALS

Submit manufacturer’s product data.

Submit dimensioned Shop Drawings and equipment ratings for voltage, capacity, horsepower, and short circuit.

DELIVERY, STORAGE and HANDLING

Deliver switches individually wrapped in factory-fabricated water-resistant type containers.

Handle switches carefully to avoid damage to material components, enclosure and finish.

Store switches in a clean, dry space protected from weather.

PRODUCTS

GENERAL

All materials shall meet or exceed all applicable referenced standards, federal, state and local requirements, and conform to codes and ordinances of authorities having jurisdiction.

MANUFACTURERS

General Electric Company.

Square D Company.

Cutler Hammer/Westinghouse.

Siemens.

FABRICATED SWITCHES

Depending upon the service indicated, use 250 or 600 volt switches, single throw, fusible, or nonfusible, horsepower rated, heavy duty, designed for locking in “ON” or “OFF” position, in code-gage steel cabinets.

Use switches which have number of poles required, dependent upon phase serving equipment.

Switches shall be NEMA 1 Underwriters’ approved for duty shown.  In wet locations, use NEMA 3R.  Where exposed to weather in exterior applications, use NEMA Krylon, corrosion resistant type.  NEMA 3R and NEMA Krylon switches shall have weatherproof threaded hubs for all conduit entries into switch.

Use fuse clips that are rejecting type to accept Class RK or L fuses.

Identify switches, as to equipment served, with engraved laminated phenolic name plates.  Refer to Section 26 01 00 for nameplate information.

EXECUTION

INSTALLATION

Installation shall meet or exceed all applicable federal, state and local requirements, referenced standards and conform to codes and ordinances of authorities having jurisdiction.

All installation shall be in accordance with manufacturer’s published recommendations.

Install safety or disconnect switches for all electrical equipment, in accordance with the applicable requirements of NEC and the National Electrical Contractors Association “Standard of Installation.”

For all equipment with motors larger than 1/8 horsepower, provide motor rated disconnect switches within sight of the motor.

Disconnect switches for such equipment shall be mounted independent of the unit to allow for maintenance access.

END OF SECTION 26 28 17